Any time you see the format of [X] [X], for example ([3/4” Fesco Board] [1/2” Retro-Fit Board], choose one of the options and erase the other.  When the specification is complete, change all the bold text to normal.  Then remove all of the brackets ([ and ]).   Note to advanced users: try the “Find and Replace” tool and replace with nil value (blank).

Every Johns Manville product listed in Part 2 is hyperlinked directly to the specific address on www.specjm.com.  Ctrl + Left Mouse Click will take you there.

SECTION 075113 - BUILT-UP ASPHALT ROOFING (BUR)

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

SECTION INCLUDES

Built-up asphalt roofing system.

Cover board.

Roof insulation

Vapor retarder.

Substrate board.

Related Sections

Edit as required.

Division 05 Section "Steel Decking" for furnishing acoustical deck rib insulation.

Division 06 Section "Miscellaneous Rough Carpentry" for wood nailers, cants, curbs, and blocking.

Division 07 Section "Sheet Metal Flashing and Trim" for metal roof penetration flashings, flashings, and counterflashings.

Division 07 Section "Manufactured Roof Expansion Joints."

Division 22 Section "Storm Drainage Piping Specialties" for roof drains.

REFERENCES

Roofing Terminology:  Refer to the following publications for definitions of roofing related terms in this Section:

ASTM D 1079 “Terminology Relating to Roofing and Waterproofing.”

Glossary of NRCA's "The NRCA Roofing and Waterproofing Manual."

Roof Consultants Institute “Glossary of Roofing Terms.”

Sheet Metal Terminology and Techniques:  SMACNA Architectural Sheet Metal Manual.

Retain below for roofing asphalt complying with ASTM D 312; insert PermaMop where required.

Hot Roofing Asphalt:  Roofing asphalt heated to its equiviscous temperature (EVT), the temperature at which its viscosity is 125 centipoise for mop-applied roofing asphalt and 75 centipoise for mechanical spreader-applied roofing asphalt, within a range of plus or minus 25 deg F (14 deg C), measured at the mop cart or mechanical spreader immediately before application.

design criteria

General:  Installed roofing membrane system shall remain watertight; and resist specified wind uplift pressures, thermally induced movement, and exposure to weather without failure.

Material Compatibility:  Roofing materials shall be compatible with one another under conditions of service and application required, as demonstrated by roofing system manufacturer based on testing and field experience.

Retain below for projects designed per ASCE 7.  Remove if Project is FMG (Factory Mutual Global) insured and retain Section D.

Wind Uplift Performance:  Roofing system shall be identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist wind uplift pressure calculated in accordance with ASCE-7.

Field-of-Roof Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Perimeter Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Corner Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Retain paragraph and subparagraphs below if Project is FMG (Factory Mutual Global) insured or if using FMG requirements as quality standard.  Remove and retain Section C if ASCE 7 requirements used.

FMG Listing:  Roofing membrane, base flashings, and component materials shall comply with requirements in FMG 4450 and FMG 4470 as part of a roofing system and that are listed in FMG's “RoofNav" for Class 1 or noncombustible construction, as applicable.  Identify materials with FMG markings.

Insert RoofNav# below.  If spec is “open”, retain FM classification for wind and hail requirements and choose applicable.  Contact Johns Manville for additional wind classification ratings, RoofNav numbers and special guarantee riders.

Roofing system shall comply with to RoofNav #:

Fire/Windstorm Classification:  Class 1A-Insert number (starting at 60 and incrementing by 15)

Hail Resistance:  [MH] [SH].

LEED Credits:

Roofing system shall be eligible for LEED Credit SS 7.1 and/or SS 7.2.

Insulation and cover board materials shall contribute to LEED credit MR 4.1

Insulation package shall contribute to LEED EA credit.

Materials with minimal VOC shall contribute to LEED credit EQ 4.

EPA Energy Star:

Roofing membrane that achieves an initial reflectance of greater than 0.65 and a three year aged reflectance of greater than 0.50.

California Code of Regulations Title 24 (T24/CRRC-1):

Provide roofing system that complies with the requirements of Title 24.

SUBMITTALS

Product Data:  Manufacturer’s data sheets for each product to be provided.

Detail Drawings:  Provide roofing system plans, elevations, sections, details, and details of attachment to other Work, including:

Adjust list below to suit Project.

Base flashings, cants, and membrane terminations.

Tapered insulation, including slopes.

Crickets, saddles, and tapered edge strips, including slopes.

Insulation fastening patterns.

Verification Samples:  Provide for each product specified.

Maintenance Data:  Refer to Johns Manville’s latest published documents on www.specJM.com.

Guarantees:  Special guarantees specified in this Section.

QUALITY ASSURANCE

Installer Qualifications:  A qualified firm that is approved, authorized, or licensed by roofing system manufacturer to install manufacturer's product and that is eligible to receive the specified manufacturer's guarantee.

Manufacturer Qualifications:  A qualified manufacturer that has [UL listing] [FMG approval] for roofing system identical to that used for this Project.

Retain paragraph below if testing agency desired and Contractor selects testing agency.

Testing Agency Qualifications:  An independent testing agency with the experience and capability to conduct the testing indicated, as documented according to ASTM E 548.

Test Reports:

Roof drain and leader test or submit plumber’s verification.

Core cut (if requested).

Roof deck fastener pullout test.

Retain moisture survey subparagraphs below for all re-roof and re-cover applications.

Moisture Survey:

Submit prior to installation, results of a non-destructive moisture test of roof system completed by approved third party.  Utilize one of the approved methods:

Infrared Thermography

Nuclear Backscatter

Source Limitations:  Obtain all components from the single source roofing system manufacturer guaranteeing the roofing system.  All products used in the system shall be labeled by the single source roofing manufacturer issuing the guarantee.

Retain subparagraph below for any project requiring torch application of membrane or flashing.

Provide evidence of CERTA training for any installer of torch-applied modified bitumen membrane.  Copies of certifications are required prior to award and must be maintained on the jobsite for inspection at any time.

Fire-Test-Response Characteristics:  Provide roofing materials with the fire-test-response characteristics indicated as determined by testing identical products per test method below by UL[, FMG,] or another testing and inspecting agency acceptable to authorities having jurisdiction.  Materials shall be identified with appropriate markings of applicable testing and inspecting agency.

If UL required, edit UL Fire requirements below.

Exterior Fire-Test Exposure:  Class  [A] [B] [C]; ASTM E 108, for application and roof slopes indicated.

Fire-Resistance Ratings:  ASTM E 119, for fire-resistance-rated roof assemblies of which roofing system is a part.

DELIVERY, STORAGE, AND HANDLING

Deliver roofing materials in original containers with seals unbroken and labeled with manufacturer's name, product brand name and type, date of manufacture, and directions for storage.

Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.

Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

Handle and store roofing materials and place equipment in a manner to avoid permanent deflection of deck.

PROJECT CONDITIONS

Weather Limitations:  Proceed with installation only when current and forecasted weather conditions permit roofing system to be installed in accordance with manufacturer's written instructions and guarantee requirements.

guarantee

Provide manufacturer's system guarantee equal to Johns Manville's Peak Advantage No Dollar Limit Roofing System Guarantee.

Retain options in subparagraph below based on those used on Project.  Verify availability of manufacturer's total-system warranty and components included.

Single-Source special guarantee includes roofing plies, flashings, roofing membrane accessories, granule surfaced roofing membrane, roof insulation, fasteners, cover board, substrate board, vapor retarder, walkway products, [manufacturer’s expansion joints], [manufacturer’s edge metal products], and other single-source components of roofing system marketed by the manufacturer.

Insert correct guarantee term.  Contact Johns Manville Technical to verify.

Guarantee Period:  [10] [15] [20] years from date of Substantial Completion.

Wind Rider:  Guarantee shall not exclude coverage for wind events up to [number between 55 - 120] mph.

Hail Rider:   Guarantee shall have no exclusions for hail events up to [1 inch] [1.5 inches] [2 inches]

Accidental Puncture Rider: Guarantee shall provide coverage for accidental puncture for up to [8] [16] billed repair hours per year for the life of the guarantee.

Installer’s Guarantee:  Submit roofing Installer's guarantee, signed by Installer, covering Work of this Section, including all components of roofing system for the following warranty period:

Guarantee Period:  Two Years from date of Substantial Completion.

PRODUCTS

ROOFING MEMBRANE PLIES

Glass-Fiber Base-Ply Sheet:  ASTM D 2178, Type [IV] [VI], asphalt-impregnated, glass-fiber felt.   Basis of Design:  [GlasPly IV] [GlasPly Premier] [or architect pre approved equal]

roofing membrane capSheet

Retain below if using granule-surfaced asphaltic cap sheet.  Remove the [reflective] if not specifying a “Cool Roof” cap sheet.

Cap Sheet:  ASTM D 3909, asphalt-impregnated and -coated, glass-fiber cap sheet, with white, [reflective,] coarse mineral-granule top surfacing and fine mineral surfacing on bottom surface.  Basis of Design: [GlasKap] [GlasKap CR] [or architect pre approved equal]

FLASHING MATERIALS

Select backer sheet, required for traditional built-up flashings behind exposed flashing sheet, from first three paragraphs below.  Coordinate selection with warranty duration.  Long-term warranties may require Type VI; verify with Johns Manville Technical Services.

Backer Sheet:  ASTM D 2178, Type  [IV] [VI], asphalt-impregnated, glass-fiber felt.  Basis of Design: [GlasPly IV] [GlasPly Premier] [or architect pre approved equal]

Select backer sheet, required for two-ply modified flashings behind exposed flashing sheet.  Contact Johns Manville Technical for flashing detail assistance.

Backer Sheet:  [ASTM D 6164, Grade S, Type I, polyester-reinforced] [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] [ASTM D 6162, Grade S, Type II, composite polyester- and glass-fiber-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaLastic 180 S] [DynaBase] [DynaPly] [or architect pre approved equal]

Retain below if coated backer sheet to be mechanically fastened over wood sheathed parapet.

Backer Sheet:  ASTM D 4601, Type II, asphalt-impregnated and -coated, glass-fiber sheet, dusted with fine mineral surfacing on both sides.  Basis of Design: PermaPly 28 [or architect pre approved equal]

Choose a granule surfaced flashing sheet below.  Specify “CR” flashing sheet if specifying “CR” membrane.

Flashing Sheet:  [ASTM D 6164, Grade G, Type II, polyester-reinforced] [ASTM D 6163, Grade G, Type I, glass-fiber-reinforced] [ASTM D 6221, Grade G, Type I, composite polyester- and glass-fiber-reinforced] [ASTM D 6298, embossed aluminum foil surfaced, glass-fiber-reinforced], SBS-modified asphalt sheet; granular surfaced; suitable for application method specified.  Basis of Design:  [DynaLastic 250 FR] [DynaLastic 250 FR CR] [DynaWeld Cap 180 FR] [DynaWeld Cap FR] [DynaWeld Cap FR CR] [DynaFlex] [DynaFlex CR] [DynaClad] [or architect pre approved equal]

Flashing sheet description in paragraph below is based on Johns Manville's "GlasTite Flexible," a proprietary asphalt-coated and smooth-surfaced flashing that requires a roof coating finish.

Flashing Sheet:  Roofing system manufacturer's asphalt-impregnated and -coated composite sheet; smooth surfaced and reinforced with a composite polyester and glass-fiber core.  Basis of Design: GlasTite Flexible [or architect pre approved equal]

AUXILIARY ROOFING MEMBRANE Materials

General:  Auxiliary materials recommended by roofing system manufacturer for intended use and compatible with built-up roofing.

Roofing Asphalt:  ASTM D 312, Type [III] [IV] [PermaMop].

Retain paragraph below if asphalt roofing cement is used to adhere flashings or integral metal sheet flashings.

Asphalt Primer:  ASTM D 41.  Basis of Design:  Asphalt Primer [or architect pre approved equal]

Asphalt Roofing Cement:  ASTM D 4586, asbestos free, of consistency required by roofing system manufacturer for application.  Basis of Design:  Bestile Industrial Roof Cement or architect pre approved equal]

Retain paragraph below if adhering base flashing  or membrane in cold-applied adhesives.

Cold-Applied Adhesive:  Roofing system manufacturer's asphalt-based, two-component, asbestos-free, cold-applied adhesive specially formulated for compatibility and use with membrane applications.  Basis of Design:  MBR Bonding Adhesive [or architect pre approved equal]

Cold-Applied Adhesive: Roofing system manufacturer's specially formulated one-part, elastomeric cold application adhesive.   Basis of Design: JM BUR Adhesive [or architect pre approved equal]

Cold-Applied Flashing Adhesive:  Roofing system manufacturer's asphalt-based, two-component, asbestos-free, trowel-grade, cold-applied adhesive specially formulated for compatibility and use with flashing applications.  Basis of Design:  MBR Flashing Cement [or architect pre approved equal]

Retain first paragraph below if sealant is needed for moving joints in sheet metal accessories or for certain locations where asphalt roofing cement may be inadequate or undesirable.

Mastic Sealant:  As required by Johns Manville.

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roofing membrane components to substrate, tested by manufacturer for required pullout strength, and provided by the roofing system manufacturer.  Basis of Design: [UltraFast Fasteners and Plates] [All Purpose Fasteners and Plates] [or architect pre approved equal]

Retain paragraph below if field-applied granules are required for incidental repairs or to coat “bleed-out” in cap sheet systems.

Roofing Granules:  Ceramic-coated roofing granules matching specified cap sheet, provided by roofing system manufacturer.

Miscellaneous Accessories:  Provide miscellaneous accessories recommended by roofing system manufacturer.

AUXILIARY ROOFING System Components

Retain subparagraph below if expansion joints are required.

Expansion Joints: Provide factory fabricated weatherproof, exterior covers for expansion joint openings consisting of flexible rubber membrane, supported by a closed cell foam to form flexible bellows, with two metal flanges, adhesively and mechanically combined to the bellows by a bifurcation process.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Expand-O-Flash] [Expand-O-Gard] [or architect pre approved equal]

Retain subparagraph below if coping flashing is required.

Coping System:  Manufacturer’s factory fabricated coping consisting of a base piece and a snap-on cap.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  Presto-Lock Coping [or architect pre approved equal]

Retain subparagraph below if fascias are required.  Specify Presto-Tite for high wind or high value projects.

Fascia System:  Manufacturer’s factory fabricated fascia consisting of a base piece and a snap-on cover.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Presto Lock Fascia] [Presto-Tite Fascia] [or architect pre approved equal]

Metal Flashing Sheet:  Metal flashing sheet is specified in Division 07 Section "Sheet Metal Flashing and Trim."

WALKWAYS

Edit as  required.

Walkway Pads:  Mineral-granule-surfaced, reinforced modified asphalt composition, slip-resisting pads, manufactured as a traffic pad for foot traffic provided by roofing system manufacturer, with a pad size of 32 inch x 32 inch.  Basis of Design: [Johns Manville DynaTred] [Johns Manville DynaTred Plus] [or architect pre approved equal]

Cover board

Select Fesco or Retro-Fit Boards for hot asphalt applications, select DuraBoard products for cold adhesive applications.

Perlite Board: ASTM C 728; composed of expanded perlite, cellulosic fibers, binders and waterproofing agents with top surface seal-coated.  Basis of Design: : [RetroPlus Roof Board] [3/4” Fesco Board] [1” Fesco Board] [1/2” Retro-Fit Board] [1/2" DuraBoard] [3/4" DuraBoard] [1" DuraBoard] [or architect pre approved equal]

ROOF INSULATION

Edit as required.  Coordinate insulation selection and thicknesses indicated on Drawings with adjoining construction, Johns Manville Guarantee requirements, as well as, HVAC design and energy program.

General:  Provide preformed roof insulation boards that comply with requirements and referenced standards, selected from manufacturer's standard sizes and of thicknesses indicated.

Polyisocyanurate Board Insulation:  ASTM C 1289, Type  II, Basis of Design: ENRGY 3 [or architect pre approved equal]

Choose performance standard or prescriptive thickness.  Remove if desired.

Provide insulation package with R Value greater than [19] [insert R Value] [minimum required by applicable code].

Provide insulation package with minimum thickness [insert thickness].

“Best practice” to retain for all.

Tapered insulation

Retain paragraph below if tapered insulation is required.  Contact Johns Manville Tapered Department for tapered designs and estimates.

Tapered Insulation:  ASTM C 1289, provide factory-tapered insulation boards fabricated to slope of [1/4 inch per 12 inches (1:48)] <Insert slope>, unless otherwise indicated.  Basis of Design: Tapered ENRGY 3 [or architect pre approved equal]

INSULATION ACCESSORIES

General:  Roof insulation accessories recommended by insulation manufacturer for intended use and compatible with membrane roofing.

Provide factory preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for sloping to drain.  Fabricate to slopes indicated. Basis of Design: [Tapered Pre-Cut Cricket] [Tapered Pre-Cut Miter] [Tapered Fesco Edge Strip] [or architect pre approved equal]

Retain below if insulation package requires mechanical fastening.

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roof insulation to substrate, and furnished by roofing system manufacturer. Basis of Design: [UltraFast Fasteners and Plates] [UltraFast Pre-Assembled Fasteners] [UltraFast AccuTrac Fastener and Plate System] [or architect pre approved equal]

Choose one of two below if adhering insulation to substrate or adhering multiple layers of insulation.  Specify for either for cold adhesive or torch applied membrane applications.

Cold Fluid-Applied Adhesive:  Manufacturer's No VOC, two-component cold fluid-applied adhesive formulated to adhere roof insulation to substrate.  Basis of Design:  MBR Bonding Adhesive [or architect pre approved equal]

Urethane Adhesive:  Manufacturer’s two component urethane adhesive formulated to adhere insulation to substrate.  Basis of Design:  [JM Two-Part Urethane Insulation Adhesive] [JM Green Two-Part Urethane Insulation Adhesive] [or architect pre approved equal]

Insulation Cant Strips:  ASTM C 728, perlite insulation board.  Basis of Design: FesCant Plus [or architect pre approved equal]

Retain paragraph below if wood nailer strips are required

Wood Nailer Strips:  Comply with requirements in Division 06 Section "Miscellaneous Rough Carpentry."

VAPOR RETARDER

Delete this Article if vapor retarders are not required.  Review compatibility of vapor retarder with other roofing system materials. Retain substrate board or layer of insulation for steel deck.

Glass-Fiber Felts:  ASTM D 2178, Type IV, asphalt-impregnated, glass-fiber felt.  Basis of Design:  [GlasPly IV] [or architect pre approved equal]

Torch Applied SBS Vapor Retarder :  [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] [ASTM D 6164, Grade S, Type I, polyester-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaWeld Base] [DynaWeld 180 S] [or architect pre approved equal]

SUBSTRATE BOARD

Select one of two substrate boards below if required or delete this Article.

Substrate Board:  ASTM C 728, perlite board, [3/4 inch (19 mm)] [1 inch (25 mm)] thick, seal coated.  Basis of Design: Fesco Board [or architect pre approved equal]

Substrate Board:  ASTM C 1177, glass-mat, water-resistant gypsum substrate, [5/8 inch (16 mm) thick. Basis of Design: JM Securock Glass Mat Roof Board [or architect pre approved equal]

EXECUTION

EXAMINATION

Examine substrates, areas, and conditions for compliance with requirements affecting performance of roofing system.

Verify that roof openings and penetrations are in place and set and braced and that roof drains are securely clamped in place.

#### Blocking, curbs, and nailers are required at edges of roof penetrations, area dividers, and terminations.

Verify that wood cants, blocking, curbs, and nailers are securely anchored to roof deck at penetrations and terminations and that nailers match thicknesses of insulation.

#### Retain subparagraph below for steel roof deck.

Verify that surface plane flatness and fastening of steel roof deck complies with requirements in Division 05 Section "Steel Decking."

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Clean and remove from substrate sharp projections, dust, debris, moisture, and other substances detrimental to roofing installation in accordance with roofing system manufacturer's written instructions.

Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Re-roof Preparation

Retain Article for Re-Roof applications.  Remove for new construction or recovers.

Remove all roofing membrane, surfacing, coverboards, insulation, fasteners, asphalt, pitch, adhesives, etc.

Remove an area no larger than can be re-roofed in one day.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.

Install decking to match existing as directed by Owner's Representative.

Raise (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Nail top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Recover Preparation

Prepare existing roof according to roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer, and requirements in this Section.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Choose one of three options below for disabling existing roof.

Disable existing roof membrane by cutting a minimum 5 foot x 5 foot grid pattern.

“Skin” existing membrane at substrate.

Remove existing membrane at fasteners.

Remove and replace wet, deteriorated or damaged roof insulation and decking as identified in moisture survey.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.  Install decking to match existing as directed by Owner's Representative.

Raise, (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Nail top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Prime existing cap sheet to prepare for recover application.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

SUBSTRATE BOARD INSTALLATION

Delete this Article if not required.

Install substrate board with long joints in continuous straight lines, perpendicular to roof slopes with end joints staggered between rows.  Tightly butt substrate boards together.

Retain one of two subparagraphs below for mechanical fastening of substrate board.  First option is for FM compliant systems.

Fasten substrate board to top flanges of steel deck according to recommendations in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten substrate board to top flanges of steel deck to resist uplift pressure at corners, perimeter, and field of roof according to roofing system manufacturer's written instructions.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

VAPOR-RETARDER INSTALLATION

Delete this Article if not required.   Retain two (2) subparagraphs below for 2 ply glass-fiber felt vapor barrier installation.

Install 2 glass-fiber felt plies lapping each sheet 19 inches (483 mm) over preceding sheet.  Embed each sheet in a solid mopping of hot roofing asphalt.  Glaze-coat completed surface with hot roofing asphalt.  Apply hot roofing asphalt at a rate of 20 lb/100 sq. ft. (1 kg/sq. m), plus or minus 25 percent.

Retain all subparagraphs below for torched SBS vapor barrier installation.

Install modified bituminous vapor retarder sheet according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, installing as follows:

Torch apply vapor retarder to substrate according to roofing system manufacturer’s instruction.

Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

Repair tears and voids in laps and lapped seams not completely sealed.

Always retain below.  To function effectively, vapor retarders or air barriers must prevent air movement into membrane roofing system.

Completely seal vapor retarder at terminations, obstructions, and penetrations to prevent air movement into membrane roofing system.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSULATION INSTALLATION

Coordinate installation of roof system components so insulation and cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with roofing system manufacturer's written instructions for installation of roof insulation and cover board.

Insulation Cant Strips:  Install and secure preformed 45-degree insulation cant strips at junctures of roofing membrane system with vertical surfaces or angle changes greater than 45 degrees per manufacturer’s instruction.

Retain first subparagraph below if tapered insulation is required.

Install tapered insulation under area of roofing to conform to slopes indicated.

Install insulation boards with long joints in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with like material.

Install one or more layers of insulation under area of roofing to achieve required thickness.  Where overall thickness is X.X inches (XX mm) or greater, install 2 or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches (150 mm) in each direction.

Trim surface of insulation boards where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Retain paragraph and subparagraphs below if mechanically fastening the first layer and adhering the remaining layers.

Mechanically Fastened with Subsequent Layers Adhered Insulation:  Secure first layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type to deck type.

Retain first subparagraph below when Project is FMG insured or FMG requirements are performance standard.  Otherwise, retain second subparagraph.

Fasten first layer according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten first layer to resist uplift pressure at corners, perimeter, and field of roof.

Install subsequent layers in a solid mopping of hot roofing asphalt according to roofing system manufacturer’s instruction.

Install subsequent layers in a cold fluid-applied adhesive according to roofing system manufacturer’s instruction.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Cover board installation

Retain Article if cover board is required for project.

Coordinate installing membrane roofing system components so cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with membrane roofing system manufacturer's written instructions for installing roof cover board.

Install cover board with long joints of cover board in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with cover board.

Cut and fit cover board within 1/4 inch (6 mm) of nailers, projections, and penetrations.

Trim surface of cover board where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Retain paragraph below if adhering cover board.  Applicable with “Adhered Insulation” and “Mechanically Fastened with Subsequent Layers Adhered” Insulation.

Adhered Cover Board:  Adhere cover board to substrate as follows:

Install in a solid mopping of hot roofing asphalt according to roofing system manufacturer’s instruction.

Install using a cold fluid-applied adhesive according to roofing system manufacturer’s instruction.

Install in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

ROOFING MEMBRANE INSTALLATION, GENERAL

Install roofing system specification 4GIC in accordance with roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer and requirements in this Section.

Delete paragraph below if not a Johns Manville Guaranteed project.

Start installation of roofing membrane in presence of roofing system manufacturer's technical personnel.

Retain paragraph and subparagraph below if roof slope exceeds minimum permitted by roofing system manufacturer.

Where roof slope exceeds 1/2 inch per 12 inches (1:24, contact the membrane manufacturer for installation instructions regarding installation direction and backnailing

Cooperate with testing and inspecting agencies engaged or required to perform services for installing roofing system.

Coordinate installing roofing system so insulation and other components of the roofing membrane system not permanently exposed are not subjected to precipitation or left uncovered at the end of the workday or when rain is imminent.

Provide tie-offs at end of each day's work to cover exposed roofing membrane sheets and insulation with a course of coated felt set in roofing cement or hot roofing asphalt with joints and edges sealed.

Complete terminations and base flashings and provide temporary seals to prevent water from entering completed sections of roofing system.

Remove and discard temporary seals before beginning work on adjoining roofing.

Retain subparagraph below for hot asphalt applications only.

Asphalt Heating:  Heat roofing asphalt and apply within plus or minus 25 deg F (14 deg C) of equiviscous temperature unless otherwise required by roofing system manufacturer.  Do not raise roofing asphalt temperature above equiviscous temperature range more than one hour before time of application.  Do not exceed roofing asphalt manufacturer's recommended temperature limits during roofing asphalt heating.  Do not heat roofing asphalt within 25 deg F (14 deg C) of flash point.  Discard roofing asphalt maintained at a temperature exceeding finished blowing temperature for more than 4 hours.

Substrate-Joint Penetrations:  Prevent roofing asphalt from penetrating substrate joints, entering building, or damaging roofing system components or adjacent building construction.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

ROOFING MEMBRANE INSTALLATION

Select number of ply sheets from options in paragraph below.

Install three ply sheets starting at low point of roofing system.  Align ply sheets without stretching.  Shingle side laps of ply sheets uniformly to achieve required number of plies throughout thickness of roofing membrane.  Shingle in direction to shed water.  Extend ply sheets over and terminate beyond cants.

Install each ply sheet in a solid mopping of hot roofing asphalt applied at rate required by roofing system manufacturer, to form a uniform membrane without ply sheets touching.

Retain paragraph and subparagraph below if surfacing roofing membrane with mineral-granule-surfaced cap sheet.  Cap sheet counts as one ply in roofing membrane ply count.

Cap Sheet:  Install lapped granulated cap sheet starting at low point of roofing system.  Offset laps from laps of preceding ply sheets and align cap sheet without stretching.  Lap in direction to shed water.  Extend cap sheet over and terminate beyond cants.

Install cap sheet in a solid mopping of hot roofing asphalt applied at rate required by roofing system manufacturer.

Proceed with installation only after unsatisfactory conditions have been corrected.

FLASHING AND STRIPPING INSTALLATION

Install base flashing over cant strips and other sloping and vertical surfaces, at roof edges, and at penetrations through roof, and secure to substrates according to roofing system manufacturer's written instructions and as follows:

Smooth surfaces of masonry and concrete walls and parapets usually require priming before applying hot asphalt or cold adhesive.

Prime substrates with asphalt primer if required by roofing system manufacturer.

Retain one of three subparagraphs below if a single backer sheet is required behind flashing sheet.  Retain first for backer sheets mechanically fastened to wood-surfaced walls or parapets and second or third for adhered backer sheets.

Backer Sheet Application:  Mechanically fasten backer sheet to walls or parapets.  Adhere backer sheet over roofing membrane at cants in a solid mopping of hot roofing asphalt.

Backer Sheet Application:  Install backer sheet and adhere to substrate in a solid mopping of hot roofing asphalt.

Backer Sheet Application:  Install backer sheet and adhere to substrate in approved adhesive applied at rate required by roofing system manufacturer.

Flashing Sheet Application:  Adhere flashing sheet to substrate in a solid mopping of hot roofing asphalt applied at EVT.  Apply hot roofing asphalt to back of flashing sheet if recommended by roofing system manufacturer.

Flashing Sheet Application:  Adhere flashing sheet to substrate in approved adhesive applied at rate required by roofing system manufacturer.

Flashing Sheet Application:  Adhere flashing sheet to substrate in approved asphalt roofing cement; apply cement at rate required by roofing system manufacturer.

Flashing Sheet Application:  Torch apply flashing sheet to substrate as required by roofing system manufacturer.

Extend base flashing up walls or parapets a minimum of 8 inches (200 mm) above roofing membrane and 4 inches (100 mm) onto field of roofing membrane.

Mechanically fasten top of base flashing securely at terminations and perimeter of roofing at a rate given by roofing system manufacturer.

Delete subparagraph below if temporarily sealing upper termination of flashings awaiting counterflashing.  Retain option if specifying termination seal.

Seal top termination of base flashing with a strip of glass-fiber fabric set in cold applied flashing adhesive.

Delete below if no interior roof drains.  Choose either lead sheet or PermaFlash.

Roof Drains:  Set [30-by-30-inch (760-by-760-mm)] <Insert size> 4 lb lead flashing sheet in a bed of MBR Flashing Cement on completed roofing membrane.  Cover metal flashing with roofing membrane cap-sheet stripping and extend a minimum of 4 inches (100 mm) beyond edge of metal flashing onto field of roofing membrane.  Clamp roofing membrane, metal flashing, and stripping into roof-drain clamping ring.

Roof Drains:  Flash drain using PermaFlash system.  Clamp roofing membrane, flashing, and stripping into roof-drain clamping ring.

Install stripping according to roofing system manufacturer's written instructions.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

WALKWAY INSTALLATION

Retain this Article if walkways set directly on roofing membrane are required.

Walkway Pads:  Install walkway pads using units of size indicated or, if not indicated, of manufacturer's standard size according to walkway pad manufacturer's written instructions.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

FIELD QUALITY CONTROL

Retain if required.

Testing Agency:  Owner will engage a qualified independent testing and inspecting agency to perform roof tests and inspections and to prepare test reports.

A roof inspection is required by Johns Manville before issuance of Johns Manville Peak Advantage Guarantee.

Final Roof Inspection:  Arrange for roofing system manufacturer's Registered Roof Observer (RRO) to inspect roofing installation on completion and submit report to Architect.

Repair or remove and replace components of roofing system where test results or inspections indicate that they do not comply with specified requirements.

Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

PROTECTIon AND CLEANING

Protect roofing system from damage and wear during remainder of construction period.

Clean overspray and spillage from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

END OF SECTION 075113