SECTION 075323 – ETHYLENE PROPYLENE DIENE MONOMER (EPDM) MEMBRANE ROOFING

- GENERAL

      - SECTION INCLUDES

        - EPDM Ballasted membrane roofing system.

        - Cover board.

        - Roof insulation.

        - Vapor retarder.

        - Substrate board.

      - Related Sections

        - Division 05 Section "Steel Decking" for roof deck.

        - Division 06 Section "Miscellaneous Rough Carpentry" for wood nailers, cants, curbs, and blocking.

        - Division 07 Section "Sheet Metal Flashing and Trim" for metal roof penetration flashings, flashings, and counter flashings.

        - Division 22 Section "Storm Drainage Piping Specialties" for roof drains.

      - REFERENCES

        - Roofing Terminology:  Refer to the following publications for definitions of roofing work related terms used in this Section:

          - ASTM D 1079 “Standard Terminology Relating to Roofing and Waterproofing.”

          - Glossary of NRCA's "The NRCA Roofing Manual."

          - Roof Consultants Institute “Glossary of Roofing Terms.”

        - Sheet Metal Terminology and Techniques:  SMACNA “Architectural Sheet Metal Manual.”

      - DESIGN CRITERIA

        - General:  Installed roofing membrane systems shall remain watertight; and resist specified wind uplift pressures, thermally induced movement, and exposure to weather without failure.

        - Material Compatibility:  Roofing materials shall be compatible with one another under conditions of service and application required, as demonstrated by roofing system manufacturer based on testing and field experience.

        - Wind Uplift Performance:  Roofing system shall be identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist wind uplift pressure calculated in accordance with ASCE 7.

          - Field-of-Roof Uplift Pressure:  	<Insert number> lbf/sq. ft. (kN/sq. m).

          - Perimeter Uplift Pressure:  	<Insert number> lbf/sq. ft. (kN/sq. m).

          - Corner Uplift Pressure:  		<Insert number> lbf/sq. ft. (kN/sq. m).

      - SUBMITTALS

        - Product Data:  Manufacturer’s data sheets for each product to be provided.

        - Detail Drawings:  Provide roofing system plans, elevations, sections, details, and details of attachment to other Work, including:

          - Base flashings, cants, and membrane terminations.

          - Tapered insulation, including slopes.

          - Crickets, saddles, and tapered edge strips, including slopes.

          - Insulation fastening patterns.

        - Verification Samples:  Provide for each product specified.

        - Installer Certificates:  Signed by roofing system manufacturer certifying that Installer is approved, authorized, or licensed by manufacturer to install roofing system.

        - Maintenance Data:  Refer to Johns Manville’s latest published documents on www.JM.com.

        - Guarantees:  Provide manufacturer’s current guarantee specimen.

      - QUALITY ASSURANCE

        - Installer Qualifications:  Qualified firm that is approved, authorized, or licensed by roofing system manufacturer to install manufacturer's product and is eligible to receive the specified manufacturer's guarantee.

        - Manufacturer Qualifications:  Qualified manufacturer that has a [UL listing] for roofing system identical to that used for this Project.

        - Testing Agency Qualifications:  Independent testing agency with the experience and capability to conduct the testing indicated, as documented in accordance with ASTM E329.

        - Test Reports:

          - Roof drain and leader test or submit plumber’s verification.

          - Core cut (if requested).

          - Roof deck fastener pullout test.

        - Moisture Survey:

          - Submit prior to installation, results of a non-destructive moisture test of roof system completed by approved third party.  Utilize one of the approved methods:

            - Infrared Thermography

            - Nuclear Backscatter

        - Source Limitations:  Obtain all components from the single source roofing system manufacturer guaranteeing the roofing system.  All products used in the system must be labeled by the single source roofing system manufacturer issuing the guarantee.

        - Fire-Test-Response Characteristics:  Roofing materials shall comply with the fire-test-response characteristics indicated as determined by testing identical products per test method below by [UL] or another testing and inspecting agency acceptable to authorities having jurisdiction.  Materials shall be identified with appropriate markings of applicable testing and inspecting agency.

          - Exterior Fire-Test Exposure:  Class [A] [B] [C]; ASTM E 108, for application and roof slopes indicated.

          - Fire-Resistance Ratings:  ASTM E 119, for fire-resistance-rated roof assemblies of which roofing system is a part.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver roofing materials in original containers with seals unbroken and labeled with manufacturer's name, product brand name and type, date of manufacture, and directions for storage.

        - Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.

        - Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

        - Handle and store roofing materials and place equipment in a manner to avoid permanent deflection of deck.

      - PROJECT CONDITIONS

        - Weather Limitations:  Proceed with installation only when current and forecasted weather conditions permit roofing system to be installed in accordance with manufacturer's written instructions and guarantee requirements.

      - guaranteeS

        - Provide manufacturer's system guarantee equal to Johns Manville's Peak Advantage No Dollar Limit Roofing System Guarantee.

          - Single-Source special guarantee includes roofing plies, base flashings, liquid applied flashing, roofing membrane accessories, [roof insulation], [fasteners], [cover board], [substrate board], [vapor retarder], [walkway products], [manufacturer’s expansion joints], [manufacturer’s edge metal products], and other single-source components of roofing system marketed by the manufacturer.

          - Guarantee Period:  [10] [15] [20] years from date of Substantial Completion.

            - Guarantee deviations must be approved in writing by roofing system manufacturer.

        - Installer’s Guarantee:  Submit roofing Installer's guarantee signed by Installer, covering Work of this Section, including all components of roofing system for the following guarantee period:

          - Guarantee Period:  [Two] [Five] Years from date of Substantial Completion.

- PRODUCTS

      - Ethylene Propylene Diene Monomer Roofing Membrane - EPDM

        - Non-reinforced uniform, flexible sheet made from Ethylene Propylene Diene Monomer, ASTM D 4637, Type I.  Basis of Design: JM EPDM NR

          - Thickness (minimum): [45 mils (1.1 mm)] [60 mils (1.5 mm)] [90 mils (2.2 mm)]

          - Exposed Face Color:  Black.

        - Scrim or fabric internally reinforced uniform, flexible sheet made from Ethylene Propylene Diene Monomer, ASTM D 4637, Type II.  Basis of Design: JM EPDM R

          - Thickness (minimum): [45 mils (1.1 mm)] [60 mils (1.5 mm)] [75 mils (1.9 mm)]

          - Exposed Face Color:  Black.

          - Factory Inseam Tape: [4 inch (101.6-mm-)] [6-inch (150-mm)] wide minimum, butyl splice tape with release film.

      - AUXILIARY Roofing Materials

        - General:  Auxiliary materials recommended by roofing system manufacturer for intended use and compatible with membrane roofing.

          - Liquid-type auxiliary materials shall meet VOC limits of authorities having jurisdiction.

        - Sheet Flashing:  Manufacturer's sheet flashing of same material, type, reinforcement, thickness, and color as sheet membrane.  Basis of Design:  JM EPDM Peel & Stick Flashing

        - Primer Material: Manufacturer’s standard synthetic-rubber polymer primer.  Basis of Design: [JM EPDM Tape Primer] [JM EPDM Tape Primer (Low VOC)]

        - Seaming Material:  Manufacturer's standard [3-inch- (75-mm-)] [6-inch- (150-mm-)] wide minimum, butyl splice tape with release film.  Basis of Design:  JM EPDM Seam Tape Plus

        - Bonding Adhesive:  Manufacturer's standard [solvent] [water]-based bonding adhesive for membrane, and solvent-based bonding adhesive for base flashings. Basis of Design:  [JM EPDM Membrane Adhesive (Low VOC)] [JM EPDM Membrane Adhesive (Solvent Based)] [JM EPDM Membrane Adhesive (Water Based)]

        - Slip Sheet:  Manufacturer's recommended slip sheet, of type required for application.

        - Metal Termination Bars:  Manufacturer's standard predrilled stainless-steel or aluminum bars, with anchors.  Basis of Design: JM Termination Systems

        - Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening membrane to substrate, and acceptable to membrane roofing system manufacturer.  Basis of Design: [High Load Fasteners and Plates] [Extra High Load Fasteners and Plates]

        - Miscellaneous Accessories:  Provide pourable sealers, preformed cone and vent sheet flashings, preformed inside and outside corner sheet flashings, T-joint covers, termination reglets, cover strips, sealants and other accessories.  Basis of Design:  [JM EPDM Peel & Stick Flashing, JM EPDM  Peel & Stick Inside/Outside Corners, JM EPDM  Peel & Stick Pipe Boots, JM EPDM  Peel & Stick Pourable Sealer Pockets, JM EPDM  Peel & Stick Sealing Strip, JM EPDM  Peel & Stick T-Joint Patch, JM EPDM  Protective Stone Mat, JM EPDM Reinforced Termination Strip with Tape (RTS),] and JM Single Ply Caulk

      - AUXILIARY ROOFING System Components

        - Expansion Joints: Provide factory fabricated weatherproof, exterior covers for expansion joint openings consisting of flexible rubber membrane, supported by a closed cell foam to form flexible bellows, with two metal flanges, adhesively and mechanically combined to the bellows by a bifurcation process.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Expand-O-Flash] [Expand-O-Gard]

        - Coping System:  Manufacturer’s factory fabricated coping consisting of a base piece and a snap-on cap.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  Presto-Lock Coping

        - Fascia System:  Manufacturer’s factory fabricated fascia consisting of a base piece and a snap-on cover.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Presto Lock Fascia] [Presto-Tite Fascia]

        - Metal Flashing Sheet:  Metal flashing sheet is specified in Division 07 Section "Sheet Metal Flashing and Trim."

      - WALKWAYS

        - Flexible Walkways:  Factory-formed, nonporous, heavy-duty, slip-resisting, surface-textured walkway pads sourced from membrane roofing system manufacturer.  Basis of Design: JM EPDM Peel & Stick Walkpads

      - Cover board

        - Perlite Board: ASTM C 728, Type 3; composed of expanded perlite, cellulosic fibers, binders and waterproofing agents with top surface seal-coated.  Basis of Design: [RetroPlus Roof Board]

        - High-Density Polyisocyanurate: ASTM C 1289, Type II, Class 4, Grade 3, High-density Polyisocyanurate technology bonded in-line to mineral-surfaced, fiber glass reinforced facers with greater than 140 lbs of compressive strength.  Basis of Design: [Invinsa Roof Board]  [Invinsa FR]

        - Gypsum Board:  ASTM C 1278, non-faced, gypsum and cellulose fiber substrate, [1/4 inch (6 mm)] [1/2 inch (13 mm)] [5/8 inch (16 mm)] thick.  Basis of Design: JM Securock Gypsum-Fiber Roof Board

        - Cement Board: ASTM C 1325, cement and glass-fiber mesh substrate, 1/2 inch (13 mm) thick. Basis of Design: JM Securock Cement Roof Board

      - ROOF INSULATION – deck Flute filler

Edit as required.  Coordinate insulation selection and thicknesses indicated on Drawings with adjoining construction, Johns Manville Guarantee requirements, as well as, HVAC design and energy program.

        - General:  Preformed roof insulation boards that comply with requirements and referenced standards, selected from manufacturer's standard sizes and of thicknesses indicated.

        - Polyisocyanurate Board Insulation:  ASTM C 1289, Type  II, Class 1, Grade 2, Product: ENRGY 3

Choose performance standard or prescriptive thickness.  Remove if desired.

          - Provide metal roof flute filler insulation package with thickness to fill flutes the height of the standing seam.

      - ROOF INSULATION

        - General:  Preformed roof insulation boards that comply with requirements and referenced standards, selected from manufacturer's standard sizes and of thicknesses indicated.

        - Polyisocyanurate Board Insulation:  ASTM C 1289, Type  II, Class [1] [2] [3], Grade [2 (20 psi)] [3 (25 psi)], Basis of Design: [ENRGY 3] [ENRGY 3 25 PSI] [ENRGY 3 CGF] [ENRGY 3 25 PSI CGF] [ENRGY 3 AGF] [ENRGY 3 25 PSI AGF] [ENRGY 3 FR] [ENRGY 3 25 PSI FR]

          - Provide insulation package with minimum R Value: [insert R Value] [minimum required by applicable code].

          - Provide insulation package with minimum thickness [insert thickness].

          - Provide insulation package in multiple layers.

          - Minimum Long-Term Thermal Resistance (LTTR): 5.7 per inch.

            - Determined in accordance with CAN/ULC S770 at 75ºF (24ºC)

      - Tapered insulation

        - Tapered Insulation:  ASTM C 1289, Type II, Class [1] [2] [3], Grade [2 (20 psi)] [3 (25 psi)], provide factory-tapered insulation boards fabricated to slope of [1/4 inch per 12 inches (1:48)] <Insert slope>, unless otherwise indicated.  Basis of Design: [Tapered ENRGY 3] [Tapered ENRGY 3 25 PSI] [Tapered ENRGY 3 CGF] [Tapered ENRGY 3 25 PSI CGF] [Tapered ENRGY 3 AGF] [Tapered ENRGY 3 25 PSI AGF] [Tapered ENRGY 3 FR] [Tapered ENRGY 3 25 PSI FR]

      - INSULATION ACCESSORIES

        - General:  Roof insulation accessories recommended by insulation manufacturer for intended use and compatible with membrane roofing.

        - Provide factory preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for sloping to drain.  Fabricate to slopes indicated. Basis of Design: [DiamondBack Pre-Cut Crickets] [DiamondBack Pre-Cut Miters] [Tapered Fesco Edge Strip]

        - Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roof insulation to substrate, and furnished by roofing system manufacturer. Basis of Design: UltraFast Fasteners and Plates

        - Two Part Urethane Adhesive:  Manufacturer’s two component polyurethane adhesive formulated to adhere insulation to substrate.  Basis of Design:  [JM Two-Part Urethane Insulation Adhesive (UIA)] [JM Green Two-Part Urethane Insulation Adhesive] [JM One-Step Foamable Adhesive]

        - One Part Urethane Adhesive: Manufacturer’s one component polyurethane adhesive formulated to adhere insulation to substrate. Basis of Design:  Urethane Insulation Adhesive

        - Wood Nailer Strips:  Comply with requirements in Division 06 Section "Miscellaneous Rough Carpentry."

      - VAPOR RETARDER

        - Glass-Fiber Felts:  ASTM D 2178, Type IV, asphalt-impregnated, glass-fiber felt.  Basis of Design:  GlasPly IV

        - Torch Applied SBS Vapor Retarder: [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] [ASTM D 6164, Grade S, Type I, polyester-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaWeld Base] [DynaBase HW] [DynaWeld 180 S]

        - Self-Adhered SBS Vapor Retarder:  ASTM D 6163, Grade S, Type I, glass-fiber-reinforced, SBS-modified asphalt sheet; sand surfaced; suitable for application method specified. Basis of Design: DynaGrip SD/SA

        - Self-Adhered SBS Vapor Retarder: Tri-laminate woven polyethylene, nonslip UV protected top surface; suitable for application method specified. Basis of Design: JM Vapor Barrier SA

        - Polyethylene Air Barrier:  ASTM D 4397, 6 mils (0.15 mm) thick, minimum, with maximum permeance rating of 0.13 perm (7.5 ng/Pa x s x sq. m).

          - Tape:  Pressure-sensitive tape of type recommended by vapor-retarder manufacturer for sealing joints and penetrations in vapor retarder.

          - Adhesive:  Manufacturer's standard lap adhesive, FMG approved for vapor-retarder application.

      - SUBSTRATE BOARD

        - Substrate Board:  ASTM C 1177, glass-mat, water-resistant gypsum substrate, 5/8 inch (16 mm) thick. Basis of Design: JM Securock Glass-Mat Roof Board

        - Substrate Board:  ASTM C 1278, non-faced, gypsum and cellulose fiber substrate, 5/8 inch (16 mm) thick.  Basis of Design: JM Securock Gypsum-Fiber Roof Board

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions for compliance with the requirements affecting performance of roofing system.

          - General:

            - Verify that roof openings and penetrations are in place and set and braced and that roof drains are securely clamped in place.

            - Verify that wood cants, blocking, curbs, and nailers are securely anchored to roof deck at penetrations and terminations and that nailers match thicknesses of insulation.

          - Steel Decks:

            - Verify that surface plane flatness and fastening of steel roof deck complies with requirements in Division 05 Section "Steel Decking."

          - Ensure general rigidity and proper slope for drainage.

          - Verify that deck is securely fastened with no projecting fasteners and with no adjacent units in excess of 1/16 inch (1.6 mm) out of plane relative to adjoining deck.

        - Unacceptable panels should be brought to the attention of the General Contractor and Project Owner’s Representative and must be corrected prior to installation of roofing system.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Clean and remove from substrate sharp projections, dust, debris, moisture, and other substances detrimental to roofing system installation in accordance with roofing system manufacturer's written instructions.

        - Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - Re-roof Preparation

        - Remove all roofing membrane, surfacing, coverboards, insulation, fasteners, asphalt, pitch, adhesives, etc.

          - Remove an area no larger than can be re-roofed in one day.

        - Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

        - Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.

          - Install decking to match existing as directed by Owner's Representative.

        - Raise (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

          - Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

          - Secure top of flashing and install new metal counterflashing prior to re-installation of unit.

          - Perimeter nailers must be elevated to match elevation of new roof insulation.

        - Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - Recover Preparation

        - Prepare existing roof according to roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer, and requirements in this Section.

        - Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

        - Disable existing roof membrane by cutting a minimum 10 foot x 10 foot grid pattern.

        - Remove existing membrane per manufacturer’s written instructions.

        - Remove and replace wet, deteriorated or damaged roof insulation and decking as identified in moisture survey.

        - Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.  Install decking to match existing as directed by Owner's Representative.

        - Raise, (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

          - Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

          - Secure top of flashing and install new metal counterflashing prior to re-installation of unit.

          - Perimeter nailers must be elevated to match elevation of new roof insulation.

        - Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

        - Prime existing membrane to prepare for recover application if applicable.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - SUBSTRATE BOARD INSTALLATION

        - Install substrate board with long joints in continuous straight lines, perpendicular to roof slopes with end joints staggered between rows.  Tightly butt substrate boards together.

          - Fasten substrate board to top flanges of steel deck to resist specified uplift pressure at corners, perimeter, and field of roof according to roofing system manufacturer's written instructions.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - VAPOR-RETARDER INSTALLATION

        - Install polyethylene-sheet vapor retarder as a loosely laid single layer over area to receive vapor retarder, side and end lapping each sheet a minimum of 2 inches (50 mm) and 6 inches (150 mm), respectively.

          - Seal side and end laps with [tape] [adhesive].

        - Install 2 glass-fiber felt plies lapping each sheet 19 inches (483 mm) over preceding sheet.  Embed each sheet in a solid mopping of hot roofing asphalt per manufacturer’s written instructions.

        - Install modified bituminous vapor retarder sheet according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, installing as follows:

          - Torch-apply vapor retarder to substrate according to roofing system manufacturer’s instruction.

          - Adhere vapor retarder in a full mopping of hot asphalt to substrate according to roofing system manufacturer’s instruction.

          - Self-adhere vapor retarder to substrate according to roofing system manufacturer’s instruction.

          - Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

        - Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

          - Repair tears and voids in laps and lapped seams not completely sealed.

        - Completely seal vapor retarder at terminations, obstructions, and penetrations to prevent air movement into membrane roofing system.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - Flute  filler INSULATION INSTALLATION

        - Coordinate installation of roof system components so insulation is not exposed to precipitation or left exposed at the end of the workday.

        - Comply with roofing system manufacturer's written instructions for installing roof insulation.

        - Loose lay Polyisocyanurate flute filler insulation between the metal roof standing seams.  Tightly butt insulation boards together.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSULATION INSTALLATION

        - Coordinate installation of roof system components so insulation and cover board is not exposed to precipitation or left exposed at the end of the workday.

        - Comply with roofing system manufacturer's written instructions for installation of roof insulation and cover board.

        - Insulation Cant Strips:  Install and secure preformed 45-degree insulation cant strips at junctures of roofing membrane system with vertical surfaces or angle changes greater than 45 degrees per manufacturer’s instruction.

        - Install tapered insulation under area of roofing to conform to slopes indicated.

        - Install insulation boards with long joints in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with like material.

        - Install 2 or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches (150 mm) in each direction.

        - Trim surface of insulation boards where necessary at roof drains so completed surface is flush and does not restrict flow of water.

        - Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

        - Preliminarily Fastened Insulation for Mechanically Fastened Systems:  Install insulation with fasteners at rate required by roofing system manufacturer or applicable authority, whichever is more stringent.

          - Fasten top layer to resist specified uplift pressure at corners, perimeter, and field of roof.

        - Adhered Insulation:  Install each layer of insulation and adhere to substrate as follows:

          - Install each layer in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

          - Install each layer in a one-part urethane adhesive according to roofing system manufacturer’s instruction.

          - Install each layer to resist specified uplift pressure at corners, perimeter, and field of roof.

        - Loose Laid Insulation with Top Insulation Layer Mechanically Fastened:  Loose lay insulation with staggered joints and secure top layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type to deck type.

          - Fasten top layer to resist specified uplift pressure at corners, perimeter, and field of roof.

        - Mechanically Fastened with Subsequent Layers Adhered Insulation:  Secure first layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type to deck type, then adhere subsequent insulation layers.

          - Fasten first layer to resist specified uplift pressure at corners, perimeter, and field of roof.

          - Install subsequent layers in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

          - Install each layer in a one-part urethane adhesive according to roofing system manufacturer’s instruction.

          - Install each layer to resist specified uplift pressure at corners, perimeter, and field of roof.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - Cover board installation

        - Coordinate installing membrane roofing system components so cover board is not exposed to precipitation or left exposed at the end of the workday.

        - Comply with membrane roofing system manufacturer's written instructions for installing roof cover board.

        - Install cover board with long joints of cover board in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with cover board.

          - Cut and fit cover board within 1/4 inch (6 mm) of nailers, projections, and penetrations.

        - Trim surface of cover board where necessary at roof drains so completed surface is flush and does not restrict flow of water.

          - Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

        - Adhered Cover Board:  Adhere cover board to substrate as follows:

          - Install in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

          - Install each layer in a one-part urethane adhesive according to roofing system manufacturer’s instruction.

          - Install to resist specified uplift pressure at corners, perimeter, and field of roof.

        - Mechanically Fastened Cover Board:  Install each layer of cover board and secure to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof cover board to deck type.

          - Fasten to resist uplift pressure at corners, perimeter, and field of roof.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - ROOFING MEMBRANE INSTALLATION, GENERAL

        - Install roofing membrane in accordance with roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer and requirements in this Section.

        - Start installation of roofing membrane in presence of roofing system manufacturer's technical personnel.

        - Cooperate with testing and inspecting agencies engaged or required to perform services for installing roofing system.

        - Coordinate installing roofing system so components of the roofing membrane system are not subjected to precipitation or left uncovered at the end of the workday or when rain is imminent.

          - Provide tie-offs at end of each day's work to cover exposed roofing membrane sheets and other components.

          - Complete terminations and base flashings and provide temporary seals to prevent water from entering completed sections of roofing system.

          - Remove and discard temporary seals before beginning work on adjoining roofing.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - LOOSELY LAID AND BALLASTED ROOFING MEMBRANE INSTALLATION

        - Install roofing membrane over area to receive roofing.

          - Unroll roofing membrane and allow to relax before installing.

          - Install sheet in accordance with roofing system manufacturer’s written instructions.

        - Start installation of roofing membrane in presence of roofing system manufacturer's technical representative.

        - Accurately align roofing membranes, without stretching, and maintain uniform side and end laps of minimum dimensions required by manufacturer.  Stagger end laps.

        - [Mechanically fasten or adhere perimeter of roofing membrane] [Adhere roofing membrane at corners, perimeters, and transitions] according to requirements in ANSI/SPRI RP-4 and according to roofing system manufacturer’s instructions.

        - Apply roofing membrane with side laps shingled with slope of deck where possible.

        - Field Fabricated Seam Installation:  Clean and prime both faces of splice areas, apply splice tape, and firmly roll side and end laps of overlapping roofing membranes according to manufacturer's written instructions to ensure a watertight seam installation.  Apply lap sealant and seal exposed edges of roofing membrane terminations.

        - Tape to Tape Installation: Align membrane for appropriate overlap, remove release liners and firmly roll side and end laps of overlapping roofing membranes according to manufacturer's written instructions to ensure a watertight seam installation.

        - Tape to Standard Sheet Installation: Align membrane for appropriate overlap, clean and prime non-taped face of splice area, remove release liners and firmly roll side and end laps of overlapping roofing membranes according to manufacturer's written instructions to ensure a watertight seam installation.

        - Leave seams uncovered until inspected by membrane roofing system manufacturer.

        - Repair tears, voids, and lapped seams in roofing that do not meet requirements.

        - Spread sealant or mastic bed over deck drain flange at deck drains and securely seal roofing membrane in place with clamping ring.

        - Install roofing membrane and auxiliary materials to tie in to existing roofing.

        - Install protection mat over roofing membrane, overlapping a minimum of 6 inches (150 mm).  Install an additional protection mat layer at projections, pipes, vents, and drains, overlapping a minimum of 12 inches (300 mm).

        - Aggregate Ballast:  Apply aggregate ballast uniformly over roofing membrane at the rate required by membrane roofing system manufacturer, but not less than the following, spreading with care to minimize possibility of damage to membrane roofing system.  Lay ballast as roofing membrane is installed, leaving roofing membrane ballasted at the end of the workday.

          - Ballast Weight:  Size 4 aggregate, 10 lb/sq. ft. (50 kg/sq. m).

          - Ballast Weight:  Size 2 aggregate, 13 lb/sq. ft. (65 kg/sq. m), at corners and perimeter; Size 4 aggregate, 10 lb/sq. ft. (50 kg/sq. m), elsewhere.

        - Roof-Paver Ballast:  Install lightweight roof-paver ballast according to manufacturer's written instructions.

        - Roof-Paver Ballast:  Install rubber roof-paver ballast according to manufacturer's written instructions, in locations indicated.

          - Install perimeter paver edge securement.

        - Roof-Paver and Aggregate Ballast:  Install heavyweight roof pavers according to manufacturer's written instructions on roof corners and perimeter.  Install Size 2 aggregate ballast elsewhere on roofing at a minimum rate of 13 lb/sq. ft. (65 kg/sq. m).

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - BASE FLASHING INSTALLATION

        - Install sheet flashings and preformed flashing accessories and adhere to substrates in accordance with membrane roofing system manufacturer's written instructions.

        - Apply bonding adhesive to substrate and underside of sheet flashing at required rate and allow to partially dry.  Do not apply bonding adhesive to seam area of flashing.

        - Flash penetrations and field-formed inside and outside corners with cured or uncured sheet flashing.

        - Terminate and seal top of sheet flashings and mechanically anchor to substrate through termination bars.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - WALKWAY INSTALLATION

        - Flexible Walkways:  Install walkway products in locations indicated.  Adhere walkway products to substrate with compatible adhesive according to roofing system manufacturer's written instructions.

        - Roof-Paver Walkways:  Install walkway roof pavers according to manufacturer's written instructions in locations indicated, to form walkways.  Leave 3 inches (75 mm) of space between adjacent roof pavers.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - FIELD QUALITY CONTROL

        - Testing Agency:  Owner will engage a qualified independent testing and inspecting agency to perform roof tests and inspections and to prepare test reports.

        - Final Roof Inspection:  Arrange for roofing system manufacturer's Registered Roof Observer (RRO) to inspect roofing installation on completion and submit report to Architect.

        - Repair or remove and replace components of roofing system where test results or inspections indicate that they do not comply with specified requirements.

      - PROTECTION AND CLEANING

        - Protect roofing system from damage and wear during remainder of construction period.

        - Correct deficiencies in or remove roofing system that does not comply with requirements, repair substrates, and repair or reinstall roofing system to a condition free of damage and deterioration at time of Substantial Completion and according to warranty requirements.

        - Clean overspray and spillage from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

END OF SECTION 075323