DELETE THIS PAGE AFTER READING

All the notes to the specifier (except this note) are in “hidden” text.  This text will not show up when printed or affect the outline formatting.  To turn the notes on, click the “Show/Hide” button pictured below located in your “Standard Toolbar”.

Any time you see the format of [X] [X], for example ([3/4” Fesco Board] [1/2” Retro-Fit Board], choose one of the options and erase the other.  When the specification is complete, change all the bold text to normal.  Then remove all of the brackets ([ and ]).   Note to advanced users: try the “Find and Replace” tool and replace with nil value (blank).

Every Johns Manville product listed in Part 2 is hyperlinked directly to the specific address on www.specjm.com.  Ctrl + Left Mouse Click will take you there.

SECTION 075419 – Polyvinyl-Chloride Roofing

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

This Section includes the following:

Adjust list below to suit Project.

Hybrid SBS base and PVC fleece-backed membrane roofing system.

Cover board.

Roof insulation.

Vapor retarder.

Substrate board.

Related Sections include the following:

Edit as required.

Division 05 Section "Steel Decking" for furnishing acoustical deck rib insulation.

Division 06 Section "[Rough Carpentry] [Miscellaneous Rough Carpentry]" for wood nailers, curbs, and blocking [and for wood-based, structural-use roof deck panels].

Division 07 Section "Thermal Insulation" for insulation beneath the roof deck.

Division 07 Section "Sheet Metal Flashing and Trim" for metal roof penetration flashings, flashings, and counterflashings.

Division 07 Section "Manufactured Roof Expansion Joints."

Division 07 Section "Joint Sealants."

Division 22 Section "Storm Drainage Piping Specialties" for roof drains.

Eliminate unit prices unless required.

Unit Prices:  Refer to Division 01 Section "Unit Prices" for description of Work in this Section affected by unit prices.

Verify no alternates in Contract. If alternates found alert Contractor and reference appropriate Division 01 Section.

DEFINITIONS

Roofing Terminology:  Refer to ASTM D 1079 “Terminology Relating to Roofing and Waterproofing”; glossary of NRCA's "The NRCA Roofing and Waterproofing Manual"; and the Roof Consultants Institute “Glossary of Roofing Terms” for definition of terms related to roofing work in this Section.

Sheet Metal Terminology and Techniques:  SMACNA Architectural Sheet Metal Manual.

PERFORMANCE REQUIREMENTS

General:  Provide installed roofing membrane and base flashings that remain watertight; do not permit the passage of water; and resist specified uplift pressures, thermally induced movement, and exposure to weather without failure.

Material Compatibility:  Provide roofing materials that are compatible with one another under conditions of service and application required, as demonstrated by roofing membrane manufacturer based on testing and field experience.

Jobsite Safety: Execute all operations and provide a safe work environment in accordance to OSHA standards and regulations.  This requirement applies to all contractor personnel, associated subcontractors, workers in other trades, and jobsite visitors.

Follow all industry fire prevention guidelines for storage of materials, staging areas, roof access, and application means and methods.

Any applicable local fire codes supersede industry guidelines.

Retain below for projects designed per ASCE 7.  Remove if Project is FMG (Factory Mutual Global) insured.

Roofing System Design:  Provide a membrane roofing system that is identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist uplift pressure calculated according to ASCE 7.

Corner Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

Perimeter Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

Field-of-Roof Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

Retain paragraph and subparagraphs below if Project is FMG (Factory Mutual Global) insured or if using FMG requirements as quality standard.

Insert RoofNav# below.  If spec is “open”, retain FM classification for wind and hail requirements and choose applicable.  Contact Johns Manville for additional wind classification ratings, RoofNav numbers and special guarantee riders.

Provide system complying to RoofNav #:

Fire/Windstorm Classification:  Class 1A-[60] [75] [90] [105] [120] <Insert number>.

Hail Resistance:  [MH] [SH].

SUBMITTALS

Product Data:  For each type of product indicated.

Shop Drawings:  For roofing system.  Include plans, elevations, sections, details, and attachments to other Work.

Adjust list below to suit Project.

Base flashings and membrane terminations.

Tapered insulation, including slopes.

Insulation fastening patterns.

Sheet layout with perimeter and corner defined.

Samples for Verification:  For the following products:

Adjust list below to suit Project.

Manufacturer’s standard sample size of sheet roofing, of color specified, including T-shaped side and end lap seam.

Manufacturer’s standard sample size of [base-ply sheet] [smooth-surfaced roofing membrane sheet] [flashing backer sheet].

Manufacturer’s standard sample size of walkway pads or rolls.

Manufacturer’s standard sample size of cover board.

Manufacturer’s standard sample size of roof insulation.

Manufacturer’s standard sample size of metal termination bars.

Manufacturer’s standard sample size of battens.

Manufacturer’s standard sample size of vapor retarder.

Manufacturer’s standard sample size of substrate board.

Six insulation fasteners of each type, length, and finish.

Six roof cover fasteners of each type, length, and finish.

Six fasteners or each type, length and finish used for complete roofing installation.

Installer Certificates:  Signed by roofing system manufacturer certifying that Installer is approved, authorized, or licensed by manufacturer to install roofing system.

Manufacturer Certificates:  Signed by roofing manufacturer certifying that roofing system complies with requirements specified in "Performance Requirements" Article.

Submit evidence of meeting performance requirements.

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

Qualification Data:  For Installer and manufacturer.

Delete below when packaged asphalt will be used.

Indicate that bulk roofing asphalt materials delivered to Project comply with requirements.  Include quantity and statistical and descriptive data for each product.  Submit certificate with each load before it is used.

Delete below when packaged asphalt will be used.

Include continuous log showing time and temperature for each load of bulk asphalt, indicating date obtained from manufacturer, where held, and how transported before final heating and application on roof.

Product Test Reports:  Based on evaluation of comprehensive tests performed by manufacturer and witnessed by a qualified testing agency, for components of roofing system.

Insert specific model code organization in first paragraph below or revise if report must be from another source.

Research/Evaluation Reports:  For components of membrane roofing system.

Maintenance Data:  For roofing system to include in maintenance manuals.

Warranties:  Special warranties specified in this Section.

QUALITY ASSURANCE

Installer Qualifications:  A qualified firm that is approved, authorized, or licensed by roofing system manufacturer to install manufacturer's product and that is eligible to receive manufacturer's warranty.

Manufacturer Qualifications:  A qualified manufacturer that has [UL listing] [FMG approval] for membrane roofing system identical to that used for this Project.

Retain paragraph below if testing agency desired and Contractor selects testing agency.

Testing Agency Qualifications:  An independent testing agency with the experience and capability to conduct the testing indicated, as documented according to ASTM E 548.

Test Reports:

Roof drain and leader test or submit plumbers verification.

Core cut (if requested).

Retain subparagraph below for all re-roof applications.

Roof deck fastener pullout test.

Retain moisture survey subparagraphs below for all re-cover applications.

Moisture Survery:

Submit prior to installation, results of a non-destructive moisture test of roof system completed by approved third party.  Utilizing one of the approved methods:

Infrared Thermography

Nuclear Backscatter

Retain first paragraph below if required to meet provisions of special manufacturer's warranty.  Consult manufacturer's literature for requirements because they vary.

Source Limitations:  Obtain all components from single source roofing manufacturer.

Fire-Test-Response Characteristics:  Provide membrane roofing materials with the fire-test-response characteristics indicated as determined by testing identical products per test method below by UL, FMG, or another testing and inspecting agency acceptable to authorities having jurisdiction.  Materials shall be identified with appropriate markings of applicable testing and inspecting agency.

If UL required, edit UL Fire requirements below.

Exterior Fire-Test Exposure:  Class  [A] [B] [C]; ASTM E 108, for application and roof slopes indicated.

Fire-Resistance Ratings:  ASTM E 119, for fire-resistance-rated roof assemblies of which roofing system is a part.

Preliminary Roofing Conference:  Before starting roof deck construction, conduct conference at Project site.  Comply with requirements for preinstallation conferences in Division 01 Section "Project Management and Coordination."  Review methods and procedures related to roof deck construction and roofing system including, but not limited to, the following:

Delete subparagraphs below not required.  If retaining, revise to include Project-specific requirements.  Insert additional requirements to suit Project.

Meet with Owner, Architect, Owner's insurer if applicable, testing and inspecting agency representative, roofing Installer, roofing system manufacturer's representative, deck Installer, and installers whose work interfaces with or affects roofing including installers of roof accessories and roof-mounted equipment.

Review methods and procedures related to roofing installation, including manufacturer's written instructions.

Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

Examine deck substrate conditions and finishes for compliance with requirements, including flatness and fastening.

Review structural loading limitations of roof deck during and after roofing.

Require that all complimentary trades be present at conference.  Including, but not limited to; electrical, plumbing, HVAC, and framing contractors.

Review base flashings, special roofing details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that will affect roofing system.

Review governing regulations and requirements for insurance and certificates if applicable.

Review temporary protection requirements for roofing system during and after installation.

Review roof observation and repair procedures after roofing installation.

Preinstallation conference below is recommended with or without preliminary roofing conference above.

Preinstallation Conference:  Conduct conference at Project site.  Comply with requirements in Division 01 Section "Project Management and Coordination."  Review methods and procedures related to roofing system including, but not limited to, the following:

Delete subparagraphs below not required.  If retaining, revise to include Project-specific requirements.  Insert additional requirements to suit Project.

Meet with Owner, Architect, Owner's insurer if applicable, testing and inspecting agency representative, roofing Installer, roofing system manufacturer's representative, deck Installer, and installers whose work interfaces with or affects roofing including installers of roof accessories and roof-mounted equipment.

Review methods and procedures related to roofing installation, including manufacturer's written instructions.

Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

Examine deck substrate conditions and finishes for compliance with requirements, including flatness and fastening.

Review structural loading limitations of roof deck during and after roofing.

Review base flashings, special roofing details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that will affect roofing system.

Review governing regulations and requirements for insurance and certificates if applicable.

Review temporary protection requirements for roofing system during and after installation.

Review roof observation and repair procedures after roofing installation.

DELIVERY, STORAGE, AND HANDLING

Deliver roofing materials to Project site in original containers with seals unbroken and labeled with manufacturer's name, product brand name and type, date of manufacture, and directions for storing and mixing with other components.

Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.  Protect stored liquid material from direct sunlight.

Discard and legally dispose of liquid material that cannot be applied within its stated shelf life.

Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Store in a dry location.  Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

Handle and store roofing materials and place equipment in a manner to avoid permanent deflection of deck.

PROJECT CONDITIONS

Weather Limitations:  Proceed with installation only when existing and forecasted weather conditions permit roofing system to be installed according to manufacturer's written instructions and warranty requirements.

guarantee

Provide manufacturer's system guarantee equal to Johns Manville's Peak Advantage No Dollar Limit Roofing System Guarantee.

Retain options in subparagraph below based on those used on Project.  Verify availability of manufacturer's total-system warranty and components included.

Single-Source special warranty includes roofing membrane, base flashings, roofing membrane accessories, [roof insulation], [fasteners], [cover board], [substrate board], [vapor retarder], [walkway products], [manufacturer’s expansion joints], [manufacturer’s edge metal products], and other single-source components of roofing system marketed by the manufacturer.

Insert correct guarantee term.  Contact Johns Manville Technical to verify.

Warranty Period:  [10] [15] [20] years from date of Substantial Completion.

Installer’s Guarantee:  Submit roofing Installer's warranty, on warranty form at end of this Section, signed by Installer, covering Work of this Section, including all components of roofing system such as roofing membrane, base flashing, roof insulation, fasteners, cover boards, substrate boards, vapor retarders, roof pavers, and walkway products, for the following warranty period:

Warranty Period:  Two years from date of Substantial Completion.

PRODUCTS

MANUFACTURER

Basis of Design: Johns Manville Roofing Systems

Polyvinyl-Chloride Roofing

PVC Sheet:  ASTM D 4434, Type III, fabric reinforced and fleece backed that contains KEE (Elvaloy) to reduce plasticizer migration.  If the membrane does not contain KEE, then a post installation coating is required to mitigate plasticizer migration. Product:  JM PVC Fleece Backed

Select one thickness in subparagraph below.  Not all guarantee terms are available for all products, coordinate with Johns Manville Technical.

Thickness:  88 mils (2.2 mm), nominal.

AUXILIARY MATERIALS

General:  Auxiliary materials recommended by roofing system manufacturer for intended use and compatible with membrane roofing.

Select VOC compliant or NO VOC application below.  Coordinate accessories selection with membrane and application.

Liquid-type auxiliary materials shall meet VOC limits of authorities having jurisdiction.

Liquid-type auxiliary materials classified as No VOC.

Retain one of two paragraphs below depending on type of roofing membrane selected.

Sheet Flashing:  Manufacturer's sheet flashing of same material, type, reinforcement, thickness, and color as sheet membrane.  Product: [JM PVC] [JM PVC Detail Strip]

Sheet Flashing:  Manufacturer's unreinforced sheet flashing of same material as sheet membrane.  Product: JM PVC Detail Membrane

Select applicable bonding adhesive below.  Coordinate with selection of "Bonding Adhesive" Paragraph in Part 3 "Adhered Roofing Membrane Installation" Article.  Coordinate proper adhesive for flashing applications with Johns Manville Technical.

Bonding Adhesive:  Manufacturer's standard [solvent] [water]-based bonding adhesive for membrane, and solvent-based bonding adhesive for base flashings. Product: [JM PVC Membrane Adhesive (Low VOC)] [JM PVC Membrane Adhesive (Water Based)]

Metal Termination Bars:  Manufacturer's standard predrilled stainless-steel or aluminum bars, with anchors.  Product: JM Termination Systems

Metal Battens:  Manufacturer's standard aluminum-zinc-alloy-coated or zinc-coated steel sheet, prepunched.  Product: Membrane Battens

Fasteners required for all applications.  Retain fasteners appropriate for application and change of plane terminations.

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening membrane to substrate, and acceptable to membrane roofing system manufacturer.  Product: [High Load Fasteners and Plates] [High Load Pre-Assembled Fasteners] [High Load Reel-Fast] [High Load AccuSeam] [Extra High Load Fasteners and Plates]

Edit as required.

Miscellaneous Accessories:  Provide pourable sealers, preformed cone and vent sheet flashings, preformed inside and outside corner sheet flashings, T-joint covers, termination reglets, cover strips, and other accessories.  Products: [JM PVC Pourable Sealer] [JM PVC Pipe Boots] [JM PVC Penetration Pan] [JM PVC Reversible Corners] [JM PVC Inside Corners] [JM PVC T-Joint Patch] [JM PVC Membrane Cleaner] [JM PVC Polyurethane Caulk] [JM PVC-Coated Metal] [JM PVC Sealant]

BASE-PLY SHEET MATERIALS

The term " base-ply sheet" is used in this Section to distinguish this part of hybrid roofing system from a conventional single ply membrane system.  Edit as required.

SBS Modified Base-Ply Sheet:  ASTM D 6164, Grade S, Type I, polyester-reinforced, SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Product: DynaLastic 180 S

Hybrid system BASE FLASHING SHEET MATERIALS

Select backer sheet from first three paragraphs below if required behind exposed flashing sheet.  Contact Johns Manville Technical for flashing detail assistance.

Retain below if coated backer sheet to be mechanically fastened over wood sheathed parapet.

Backer Sheet:  ASTM D 4601, Type  II, asphalt-impregnated and -coated, glass-fiber sheet, dusted with fine mineral surfacing on both sides.  Product: PermaPly 28

Select backer sheet from paragraph below for first ply of a two-ply flashing system for use with hybrid specifications.  Contact Johns Manville Technical for flashing detail assistance.

Backer Sheet:  ASTM D 6164, Grade S, Type I, polyester-reinforced, SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Product: DynaLastic 180 S

Flashing Sheet:  Specified membrane material.

WALKWAYS

Flexible Walkways:  Factory-formed, nonporous, heavy-duty, slip-resisting, surface-textured walkway pads sourced from membrane roofing system manufacturer.  Product: [JM PVC Heavy-Duty Walkpad] [JM PVC Walkpad]

Cover board

Retain Article for applications requiring coverboard.  Choose one option below.

Perlite Board: ASTM C 728; composed of expanded perlite, cellulosic fibers, binders and waterproofing agents with top surface seal-caoted.  Product: : [3/4” Fesco Board] [1” Fesco Board] [1/2” Retro-Fit Board] [3/4" DuraBoard] [1" DuraBoard]

ROOF INSULATION

Edit as required.  Coordinate insulation selection and thicknesses indicated on Drawings with adjoining construction, Johns Manville Guarantee requirements, as well as, HVAC design and energy program.

General:  Provide preformed roof insulation boards that comply with requirements and referenced standards, selected from manufacturer's standard sizes and of thicknesses indicated.

Polyisocyanurate Board Insulation:  ASTM C 1289, Type  II, Product: ENRGY 3

Choose performance standard or prescriptive thickness.  Remove if desired.

Provide insulation package with R Value greater than [19] [insert R Value] [minimum required by applicable code].

Provide insulation package with minimum thickness [insert thickness].

“Best practice” to retain for all.

Install no boards thicker than 1.5”.  If insulation package required is thicker than 1.5”, install in multiple layers.

Tapered insulation

Retain paragraph below if tapered insulation is required.  Contact Johns Manville Tapered Department for tapered designs and estimates.

Tapered Insulation:  ASTM C 1289, rovide factory-tapered insulation boards fabricated to slope of [1/4 inch per 12 inches (1:48)] <Insert slope>, unless otherwise indicated.  Product: Tapered ENRGY 3

INSULATION ACCESSORIES

General:  Roof insulation accessories recommended by insulation manufacturer for intended use and compatible with membrane roofing.

Provide factory preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for sloping to drain.  Fabricate to slopes indicated. Product: [Tapered Pre-Cut Cricket] [Tapered Pre-Cut Miter] [Tapered Fesco Edge Strip]

Retain below if insulation package requires mechanical fastening.

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roof insulation to substrate, and provided by roofing system manufacturer. Product: [UltraFast Fasteners and Plates] [UltraFast Pre-Assembled Fasteners] [UltraFast AccuTrac Fastener and Plate System]

Choose one of two below if adhering insulation to substrate or adhering multiple layers of insulation.  Specify for either for cold adhesive or torch applied membrane applications.

Cold Fluid-Applied Adhesive:  Manufacturer's No VOC, two-component cold fluid-applied adhesive formulated to adhere roof insulation to substrate.  Product:  MBR Bonding Adhesive

Urethane Adhesive:  Manufacturer’s two component urethane adhesive formulated to adhere insulation to substrate.  Product:  [JM Two-Part Urethane Insulation Adhesive] [JM Green Two-Part Urethane Insulation Adhesive]

Insulation Cant Strips:  ASTM C 728, perlite insulation board.  Product: FesCant Plus

Retain paragraph below if wood nailer strips are required

Wood Nailer Strips:  Comply with requirements in Division 06 Section "[Rough Carpentry] [Miscellaneous Rough Carpentry]."

VAPOR RETARDER

Delete this Article if vapor retarders are not required.  Retain substrate board for vapor retarders over a steel deck.

Retain below for applications requiring a vapor barrier and no hot asphalt is specified for project.

Torch Applied SBS Vapor Retarder :  [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] [ASTM D 6164, Grade S, Type I, polyester-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Product: [DynaWeld Base] [DynaWeld 180 S]

Retain below for standard two-ply vapor retarder in hot asphalt.

Glass-Fiber Felts:  ASTM D 2178, Type IV, asphalt-impregnated, glass-fiber felt.  Product: [GlasPly IV]

SUBSTRATE BOARD

Select one of two substrate boards below if required or delete this Article.

Substrate Board:  ASTM C 1177/C 1177M, glass-mat, water-resistant gypsum substrate, [1/4 inch (6 mm)] [1/2 inch (13 mm)] [5/8 inch (16 mm)] thick.  Product: Securock.

Substrate Board:  ASTM C 728, perlite board, [3/4 inch (19 mm)] [1 inch (25 mm)] thick, seal coated.  Product: Fesco Board.

Retain below when attaching substrate board.  Edit as required.

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening substrate panel to roof deck.  Product: [UltraFast Fasteners and Plates] [UltraFast Pre-Assembled Fasteners] ]UltraFast AccuTrac Fastener and Plate System]

EXECUTION

EXAMINATION

Examine substrates, areas, and conditions, with Installer present, for compliance with the following requirements and other conditions affecting performance of roofing system:

Verify that roof openings and penetrations are in place and set and braced and that roof drains are securely clamped in place.

Blocking, curbs, and nailers are required at edges of roof penetrations, area dividers, and terminations.

Verify that wood cants, blocking, curbs, and nailers are securely anchored to roof deck at penetrations and terminations and that nailers match thicknesses of insulation.

Verify that surface plane flatness and fastening of steel roof deck complies with requirements in Division 05 Section "Steel Decking."

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Clean substrate of dust, debris, moisture, and other substances detrimental to roofing installation according to roofing system manufacturer's written instructions.  Remove sharp projections.

Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.  Remove roof-drain plugs when no work is taking place or when rain is forecast.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Re-roof Preparation

Retain Article for Re-Roof applications

Remove all roofing membrane, surfacing, coverboards, insulation, fasteners, asphalt, pitch, adhesives, etc.

Remove an area no larger than can be re-roofed in one day.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.

Install decking to match existing as directed by Owner's Representative.

Raise, (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Nail top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

SUBSTRATE BOARD INSTALLATION

Delete this Article if not required.

Install substrate board with long joints in continuous straight lines, perpendicular to roof slopes with end joints staggered between rows.  Tightly butt substrate boards together.

Retain one of two subparagraphs below for mechanical fastening of substrate board.  First option

Fasten substrate board to top flanges of steel deck according to recommendations in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten substrate board to top flanges of steel deck to resist uplift pressure at corners, perimeter, and field of roof according to roofing system manufacturer's written instructions.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

VAPOR-RETARDER INSTALLATION

Delete this Article if not required.  Retain selected vapor-retarder material from paragraphs below.

Retain all subparagraphs below for torched SBS vapor barrier installation.

Install modified bituminous vapor retarder sheet according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, installing as follows:

Torch apply to substrate.

Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

Repair tears and voids in laps and lapped seams not completely sealed.

Apply roofing granules to cover exuded bead at laps while bead is hot.

Retain two (2) subparagraphs below for 2 ply glass-fiber felt vapor barrier installation.

Install 2 glass-fiber felt plies lapping each sheet 19 inches (483 mm) over preceding sheet.  Embed each sheet in a solid mopping of hot roofing asphalt.  Glaze-coat completed surface with hot roofing asphalt.  Apply hot roofing asphalt at a rate of 20 lb/100 sq. ft. (1 kg/sq. m), plus or minus 25 percent.

Completely seal vapor retarder at terminations, obstructions, and penetrations to prevent air movement into roofing system.

Always retain below.  To function effectively, vapor retarders or air barriers must prevent air movement into membrane roofing system.

Completely seal vapor retarder at terminations, obstructions, and penetrations to prevent air movement into membrane roofing system.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSULATION INSTALLATION

Coordinate installing roof system components so insulation is not exposed to precipitation or left exposed at the end of the workday.

Comply with roofing system manufacturer's written instructions for installing roof insulation.

Insulation Cant Strips:  Install and secure preformed 45-degree insulation cant strips at junctures of roofing membrane system with vertical surfaces or angle changes greater than 45 degrees per manufacturer’s instruction.

Retain first subparagraph below if tapered insulation is required.

Install tapered insulation under area of roofing to conform to slopes indicated.

Install insulation with long joints of insulation in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with insulation.

Cut and fit insulation within 1/4 inch (6 mm) of nailers, projections, and penetrations.

Install one or more layers of insulation under area of roofing to achieve required thickness.  Where overall insulation thickness is 1.5 inches (38 mm) or greater, install 2 or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches (150 mm) in each direction.

Trim surface of insulation where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Retain paragraph below for preliminarily fastening Insulation.  Use for Loose Laid Insulation, as well.

Preliminarily Fastened Insulation:  Install cover board with fasteners at rate required by roofing system manufacturer or applicable authority, which ever is more stringent.

Retain paragraph below if mechanically fastening insulation layers.

Mechanically Fastened Insulation:  Secure uppermost layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof insulation to deck type.  Loose lay all other layers below with staggered joints.

Retain first subparagraph below when Project is FMG insured or FMG requirements are performance standard.  Otherwise, retain second subparagraph.

Fasten according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten to resist uplift pressure at corners, perimeter, and field of roof.

Retain paragraph and subparagraphs below if mechanically fastening the first layer and adhering the remaining layers.

Mechanically Fastened with Subsequent Layers Adhered Insulation:  Secure first layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof insulation to deck type.

Retain first subparagraph below when Project is FMG insured or FMG requirements are performance standard.  Otherwise, retain second subparagraph.

Fasten first layer according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten first layer to resist uplift pressure at corners, perimeter, and field of roof.

Select one of two subparagraphs below.

Install subsequent layers in a solid mopping of hot roofing asphalt.

Install subsequent layers in a cold fluid-applied adhesive.

Install subsequent layers in a two-part urethane adhesive.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Cover board installation

Coordinate installing membrane roofing system components so cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with membrane roofing system manufacturer's written instructions for installing roof cover board.

Install cover board with long joints of cover board in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with cover board.

Cut and fit cover board within 1/4 inch (6 mm) of nailers, projections, and penetrations.

Trim surface of cover board where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Retain paragraph below if adhering cover board.  Applicable with “Adhered Insulation” and “Mechanically Fastened with Subsequent Layers Adhered” Insulation.

Adhered Cover Board:  Adhere cover board to substrate as follows:

Retain applicable subparagraphs below.

Set each layer in a solid mopping of hot roofing asphalt.

Set in a two-part cold fluid-applied adhesive according to roofing system manufacturer’s instruction.

Set in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Retain paragraph below if mechanically fastening cover board layer.  Applicable with “Preliminarily Fastened Insulation” and “Loosely Laid Insulation”.

Mechanically Fastened Cover Board:  Install each layer of cover board and secure to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof cover board to deck type.

Retain first subparagraph below when Project is FMG insured or FMG requirements are performance standard.  Otherwise, retain second subparagraph.

Fasten according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten to resist uplift pressure at corners, perimeter, and field of roof.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

BASE-PLY SHEET INSTALLATION

Install two plies of modified bituminous base-ply sheet according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend base-ply sheets over and terminate beyond cants, installing as follows:

Select one subparagraphs below.

Adhere to substrate in a solid mopping of hot roofing asphalt applied at not less than 425 deg F (218 deg C).

Torch apply to substrate.

Retain for all.

Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

Repair tears and voids in laps and lapped seams not completely sealed.

Apply roofing granules to cover exuded bead at laps while bead is hot.

Install roofing membrane sheets so side and end laps shed water.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

ADHERED ROOFING MEMBRANE INSTALLATION

Install roofing membrane over area to receive roofing according to membrane roofing system manufacturer's written instructions.  Unroll roofing membrane and allow to relax before installing.

Install sheet according to ASTM D 5036 and Johns Manville’s “Single Ply Roofing” Binder.

Delete first paragraph below if not applicable.

Start installation of roofing membrane in presence of membrane roofing system manufacturer's technical personnel.

Accurately align roofing membrane and maintain uniform side and end laps of minimum dimensions required by manufacturer.  Stagger end laps.

Hot Asphalt Application:  Adhere to substrate in a solid mopping of hot roofing asphalt applied at not less than 425 deg F (218 deg C).

Install membrane using either roll or fold method.  Refer to Johns Manville Single Ply Binder for details.

“Broom” the sheet in to ensure full contact.  Do not walk on membrane.

Mechanically fasten roofing membrane securely at terminations, penetrations, and perimeter of roofing.

Apply roofing membrane with side laps shingled with slope of roof deck where possible.

Seams:  Clean seam areas, overlap roofing membrane, and hot-air weld side and end laps of roofing membrane according to manufacturer's written instructions to ensure a watertight seam installation.

Test lap edges with probe to verify seam weld continuity.  Apply lap sealant to seal cut edges of roofing membrane.

Verify field strength of seams a minimum of twice daily and repair seam sample areas.

Remove and repair any unsatisfactory sections before proceeding with Work.

Repair tears, voids, and lapped seams in roofing membrane that do not meet requirements.

Spread sealant or mastic bed over deck drain flange at deck drains and securely seal roofing membrane in place with clamping ring.

Retain below if tie-ins to existing roofing are required.

Install roofing membrane and auxiliary materials to tie in to existing roofing.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

BASE FLASHING INSTALLATION

Install sheet flashings and preformed flashing accessories and adhere to substrates according to membrane roofing system manufacturer's written instructions.

Apply solvent-based bonding adhesive to substrate and underside of sheet flashing at required rate and allow to partially dry.  Do not apply bonding adhesive to seam area of flashing.

Flash penetrations and field-formed inside and outside corners with sheet flashing.

Clean seam areas and overlap and firmly roll sheet flashings into the adhesive.  Weld side and end laps to ensure a watertight seam installation.

Terminate and seal top of sheet flashings and mechanically anchor to substrate through termination bars.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

WALKWAY INSTALLATION

Delete this Article if walkways are not required.

Flexible Walkways:  Install walkway products in locations indicated.  Heat weld to substrate or adhere walkway products to substrate with compatible adhesive according to roofing system manufacturer's written instructions.

FIELD QUALITY CONTROL

Retain if required.

Testing Agency:  Owner will engage a qualified independent testing and inspecting agency to perform roof tests and inspections and to prepare test reports.

A roof inspection is required by Johns Manville before issuance of Johns Manville Peak Advantage Guarantee.

Final Roof Inspection:  Arrange for roofing system manufacturer's technical personnel to inspect roofing installation on completion and submit report to Architect.

Retain subparagraph below if Architect or Owner wants to be present during manufacturer's final inspection.

Notify Architect or Owner 48 hours in advance of date and time of inspection.

Repair or remove and replace components of membrane roofing system where test results or inspections indicate that they do not comply with specified requirements.

Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

PROTECTING AND CLEANING

Protect membrane roofing system from damage and wear during remainder of construction period.  When remaining construction will not affect or endanger roofing, inspect roofing for deterioration and damage, describing its nature and extent in a written report, with copies to Architect and Owner.

Correct deficiencies in or remove membrane roofing system that does not comply with requirements, repair substrates, and repair or reinstall membrane roofing system to a condition free of damage and deterioration at time of Substantial Completion and according to warranty requirements.

Clean overspray and spillage from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

END OF SECTION 075419