SECTION 075419 – POLYVINYL CHLORIDE (PVC) MEMBRANE ROOFING

GENERAL

SECTION INCLUDES

PVC Adhered membrane roofing system.

Cover board.

Roof insulation.

Vapor retarder.

Substrate board.

Related Sections:

Division 05 Section "Steel Decking" for furnishing acoustical deck rib insulation.

Division 06 Section "Miscellaneous Rough Carpentry" for wood nailers, cants, curbs, and blocking[ and for wood-based, structural-use roof deck panels].

Division 07 Section "Sheet Metal Flashing and Trim" for metal roof penetration flashings, flashings, and counterflashings.

Division 07 Section "Manufactured Roof Expansion Joints."

Division 22 Section "Storm Drainage Piping Specialties" for roof drains.

REFERENCES

Roofing Terminology:  Refer to the following publications for definitions of roofing work related terms used in this Section:

ASTM D 1079 “Terminology Relating to Roofing and Waterproofing.”

Glossary of NRCA's "The NRCA Roofing and Waterproofing Manual."

Roof Consultants Institute “Glossary of Roofing Terms.”

Sheet Metal Terminology and Techniques:  SMACNA Architectural Sheet Metal Manual.

Hot Roofing Asphalt:  Roofing asphalt heated to its equiviscous temperature (EVT), the temperature at which its viscosity is 125 centipoise for mop-applied roofing asphalt and 75 centipoise for mechanical spreader-applied roofing asphalt, within a range of plus or minus 25 deg F (14 deg C), measured at the mop cart or mechanical spreader immediately before application.

DESIGN CRITERIA

General:  Installed roofing membrane and base flashing systems shall remain watertight; and resist specified wind uplift pressures, thermally induced movement, and exposure to weather without failure.

Material Compatibility:  Roofing materials shall be compatible with one another under conditions of service and application required, as demonstrated by roofing system manufacturer based on testing and field experience.

Wind Uplift Performance:  Roofing system shall be identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist wind uplift pressure calculated in accordance with ASCE-7.

Field-of-Roof Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Perimeter Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Corner Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

FMG Listing:  Roofing membrane, base flashings, and component materials shall comply with requirements in FMG 4450 and FMG 4470 as part of a roofing system and that are listed in FMG's “RoofNav" for Class 1 or noncombustible construction, as applicable.  Identify materials with FMG markings.

Roofing system shall comply with RoofNav #:

Fire/Windstorm Classification:  Class 1A-Insert number (starting at 60 and incrementing by 15)

Hail Resistance:  [MH] [SH].

LEED Credits:

Roofing system shall be eligible for LEED Credit SS 7.1 and/or SS 7.2.

Insulation and cover board materials shall contribute to LEED credit MR 4.1

Insulation package shall contribute to LEED EA credit.

Materials with minimal VOC shall contribute to LEED credit EQ 4.

EPA Energy Star:

Roofing membrane shall achieve an initial reflectance of greater than 0.65 and a three year aged reflectance of greater than 0.50.

T24/CRRC-1:

Roofing system shall comply with the requirements of Title 24.

Roofing membrane shall be tested by CRRC-1.

SUBMITTALS

Product Data:  Manufacturer’s product data sheets for each product to be provided.

Detail Drawings:  Provide roofing system plans, elevations, sections, details, and details of attachment to other Work, including:

Base flashings, cants, and membrane terminations.

Tapered insulation, including slopes.

Crickets, saddles, and tapered edge strips, including slopes.

Insulation fastening patterns.

Verification Samples:  Provide for each product specified.

Maintenance Data:  Refer to Johns Manville’s latest published documents on www.specJM.com.

Guarantees:  Special guarantees specified in this Section.

QUALITY ASSURANCE

Installer Qualifications:  Qualified firm that is approved, authorized, or licensed by roofing system manufacturer to install manufacturer's product and is eligible to receive the specified manufacturer's guarantee.

Manufacturer Qualifications:  Qualified manufacturer that has [UL listing] [FMG approval] for roofing system identical to that used for this Project.

Testing Agency Qualifications:  Independent testing agency with the experience and capability to conduct the testing indicated, as documented in accordance with ASTM E 548.

Test Reports:

Roof drain and leader test or submit plumber’s verification.

Core cut (if requested).

Roof deck fastener pullout test.

Moisture Survey:

Submit prior to installation, results of a non-destructive moisture test of roof system completed by approved third party.  Utilize one of the approved methods:

Infrared Thermography

Nuclear Backscatter

Source Limitations:  Obtain all components from the single source roofing system manufacturer guaranteeing the roofing system.  All products used in the system shall be labeled by the single source roofing system manufacturer issuing the guarantee.

Fire-Test-Response Characteristics:  Roofing materials shall comply with the fire-test-response characteristics indicated as determined by testing identical products per test method below by UL, [FMG], or another testing and inspecting agency acceptable to authorities having jurisdiction.  Materials shall be identified with appropriate markings of applicable testing and inspecting agency.

Exterior Fire-Test Exposure:  Class  [A] [B] [C]; ASTM E 108, for application and roof slopes indicated.

Fire-Resistance Ratings:  ASTM E 119, for fire-resistance-rated roof assemblies of which roofing system is a part.

DELIVERY, STORAGE, AND HANDLING

Deliver roofing materials in original containers with seals unbroken and labeled with manufacturer's name, product brand name and type, date of manufacture, and directions for storage.

Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.

Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

Handle and store roofing materials and place equipment in a manner to avoid permanent deflection of deck.

PROJECT CONDITIONS

Weather Limitations:  Proceed with installation only when current and forecasted weather conditions permit roofing system to be installed in accordance with manufacturer's written instructions and guarantee requirements.

guaranteeS

Provide manufacturer's system guarantee equal to Johns Manville's Peak Advantage No Dollar Limit Roofing System Guarantee.

Single-Source special guarantee includes roofing plies, base flashings, liquid applied flashing, roofing membrane accessories, [roof insulation], [fasteners], [cover board], [substrate board], [vapor retarder], [walkway products], [manufacturer’s expansion joints], [manufacturer’s edge metal products], and other single-source components of roofing system marketed by the manufacturer.

Guarantee Period:  [10] [15] [20] years from date of Substantial Completion.

Wind Rider:  Guarantee shall not exclude coverage for wind events up to [number between 55 - 120] mph.

Hail Rider:   Guarantee shall have no exclusions for hail events up to [1 inch] [1.5 inches] [2 inches]

Accidental Puncture Rider: Guarantee shall provide coverage for accidental puncture for up to [8] [16] billed repair hours per year for the life of the guarantee.

Installer’s Guarantee:  Submit roofing Installer's guarantee signed by Installer, covering Work of this Section, including all components of roofing system, for the following guarantee period:

Guarantee Period:  [Two] [Five] Years from date of Substantial Completion.

PRODUCTS

Polyvinyl-Chloride Roofing Membrane - PVC

PVC Sheet:  ASTM D 4434, Type III, fabric reinforced that contains KEE (Elvaloy) to reduce plasticizer migration.  Basis of Design:  [JM PVC Fleece Backed] [or architect pre approved equal]

If the membrane does not contain KEE, then a post installation coating is required to mitigate plasticizer migration..

Certification, by letter, stating that the formulation has a minimum 15 years of performance history in North America.

Thickness: 88 mils (2.24mm), minimum] 88 mils (2.24mm), nominal

AUXILIARY Roofing Materials – Single Ply

General:  Auxiliary materials recommended by roofing system manufacturer for intended use and compatible with membrane roofing.

Liquid-type auxiliary materials shall meet VOC limits of authorities having jurisdiction.

Sheet Flashing:  Manufacturer's sheet flashing of same material, type, reinforcement, thickness, and color as sheet membrane.  Basis of Design: [JM PVC] [JM PVC Detail Strip] [or architect pre approved equal]

Sheet Flashing:  Manufacturer's unreinforced sheet flashing of same material as sheet membrane.  Basis of Design: [JM PVC Detail Membrane] [or architect pre approved equal]

Bonding Adhesive:  Manufacturer's standard [solvent] [water]-based bonding adhesive for membrane, and solvent-based bonding adhesive for base flashings. Basis of Design: [JM PVC Membrane Adhesive (Low VOC)] [JM PVC Membrane Adhesive (Water Based)] [or architect pre approved equal]

Slip Sheet:  Manufacturer's recommended slip sheet, of type required for application.

Metal Termination Bars:  Manufacturer's standard predrilled stainless-steel or aluminum bars, with anchors.  Basis of Design: JM Termination Systems [or architect pre approved equal]

Metal Battens:  Manufacturer's standard aluminum-zinc-alloy-coated or zinc-coated steel sheet, prepunched.  Basis of Design: Membrane Battens [or architect pre approved equal]

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening membrane to substrate, and acceptable to membrane roofing system manufacturer.  Basis of Design: [High Load Fasteners and Plates] [High Load Pre-Assembled Fasteners] [High Load Reel-Fast] [High Load AccuSeam] [Extra High Load Fasteners and Plates] [or architect pre approved equal]

Miscellaneous Accessories:  Provide pourable sealers, preformed cone and vent sheet flashings, preformed inside and outside corner sheet flashings, T-joint covers, termination reglets, cover strips, sealants, and other accessories.  Basis of Design: [JM PVC Pourable Sealer, JM PVC Pipe Boots, JM PVC Penetration Pan, JM PVC Reversible Corners, JM PVC Inside Corners, JM PVC T-Joint Patch, JM PVC Membrane Cleaner, JM PVC-Coated Metal, JM PVC Sealant] and JM Single Ply Caulk [or architect pre approved equals]

AUXILIARY ROOFING System Components

Expansion Joints: Provide factory fabricated weatherproof, exterior covers for expansion joint openings consisting of flexible rubber membrane, supported by a closed cell foam to form flexible bellows, with two metal flanges, adhesively and mechanically combined to the bellows by a bifurcation process.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Expand-O-Flash] [Expand-O-Gard] [or architect pre approved equal]

Coping System:  Manufacturer’s factory fabricated coping consisting of a base piece and a snap-on cap.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  Presto-Lock Coping [or architect pre approved equal]

Fascia System:  Manufacturer’s factory fabricated fascia consisting of a base piece and a snap-on cover.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Presto Lock Fascia] [Presto-Tite Fascia] [or architect pre approved equal]

Metal Flashing Sheet:  Metal flashing sheet is specified in Division 07 Section "Sheet Metal Flashing and Trim."

WALKWAYS

Flexible Walkways:  Factory-formed, nonporous, heavy-duty, slip-resisting, surface-textured walkway pads sourced from membrane roofing system manufacturer.  Basis of Design: [JM PVC Heavy-Duty Walkpad] [JM PVC Walkpad] [or architect pre approved equal]

Cover board

Perlite Board: ASTM C 728; composed of expanded perlite, cellulosic fibers, binders and waterproofing agents with top surface seal-coated.  Basis of Design: : [RetroPlus Roof Board] [3/4” Fesco Board] [1” Fesco Board] [1/2” Retro-Fit Board] [1/2" DuraBoard] [3/4" DuraBoard] [1" DuraBoard] [or architect pre approved equal]

High-Density Polyisocyanurate: High-density polyisocyanurate technology bonded in-line to mineral-surfaced, fiber glass reinforced facers with greater than 125 lbs of compressive strength.  Basis of Design: Invinsa Roof Board [or architect pre approved equal]

Gypsum Board:  ASTM C1177, glass-mat faced, water-resistant gypsum substrate, [1/4 inch (6 mm)] [1/2 inch (13 mm)] [5/8 inch (16 mm)] thick.  Basis of Design: JM Securock Glass Mat Roof Board [or architect pre approved equal]

Gypsum Board:  ASTM C1278, non-faced, gypsum and cellulose fiber substrate, [1/4 inch (6 mm)] [1/2 inch (13 mm)] [5/8 inch (16 mm)] thick.  Basis of Design: JM Securock Gypsum-Fiber Roof Board [or architect pre approved equal]

ROOF INSULATION

General:  Provide preformed roof insulation boards that comply with requirements and referenced standards, selected from manufacturer's standard sizes and of thicknesses indicated.

Polyisocyanurate Board Insulation:  ASTM C 1289, Type  II, Basis of Design: ENRGY 3 [or architect pre approved equal]

Provide insulation package with R Value greater than [19] [insert R Value] [minimum required by applicable code].

Provide insulation package with minimum thickness [insert thickness].

Tapered insulation

Tapered Insulation:  ASTM C 1289, provide factory-tapered insulation boards fabricated to slope of [1/4 inch per 12 inches (1:48)] <Insert slope>, unless otherwise indicated.  Basis of Design: Tapered ENRGY 3 [or architect pre approved equal]

INSULATION ACCESSORIES

General:  Roof insulation accessories recommended by insulation manufacturer for intended use and compatible with membrane roofing.

Provide factory preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for sloping to drain.  Fabricate to slopes indicated. Basis of Design: [Tapered Pre-Cut Cricket] [Tapered Pre-Cut Miter] [Tapered Fesco Edge Strip] [or architect pre approved equal]

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roof insulation to substrate, and furnished by roofing system manufacturer. Basis of Design: [UltraFast Fasteners and Plates] [UltraFast Pre-Assembled Fasteners] [UltraFast AccuTrac Fastener and Plate System] [or architect pre approved equal]

Urethane Adhesive:  Manufacturer’s two component urethane adhesive formulated to adhere insulation to substrate.  Basis of Design:  [JM Two-Part Urethane Insulation Adhesive] [JM Green Two-Part Urethane Insulation Adhesive] [or architect pre approved equal]

Wood Nailer Strips:  Comply with requirements in Division 06 Section "Miscellaneous Rough Carpentry."

AUXILIARY ROOFING MEMBRANE - Bituminous

Roofing Asphalt:  ASTM D 312, Type [III] [IV] [PermaMop].

VAPOR RETARDER

Glass-Fiber Felts:  ASTM D 2178, Type IV, asphalt-impregnated, glass-fiber felt.  Basis of Design:  [GlasPly IV] [or architect pre approved equal]

Torch Applied SBS Vapor Retarder:  [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] [ASTM D 6164, Grade S, Type I, polyester-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaWeld Base] [DynaWeld 180 S] [or architect pre approved equal]

Polyethylene Air Barrier:  ASTM D 4397, 6 mils (0.15 mm) thick, minimum, with maximum permeance rating of 0.13 perm (7.5 ng/Pa x s x sq. m).

Tape:  Pressure-sensitive tape of type recommended by vapor-retarder manufacturer for sealing joints and penetrations in vapor retarder.

Adhesive:  Manufacturer's standard lap adhesive, FMG approved for vapor-retarder application.

SUBSTRATE BOARD

Substrate Board:  ASTM C 728, perlite board, [3/4 inch (19 mm)] [1 inch (25 mm)] thick, seal coated.  Basis of Design: Fesco Board [or architect pre approved equal]

Substrate Board:  ASTM C 1177, glass-mat, water-resistant gypsum substrate, [5/8 inch (16 mm) thick. Basis of Design: JM Securock Glass Mat Roof Board [or architect pre approved equaRetain below with substrate board selected from paragraphs above.

EXECUTION

EXAMINATION

Examine substrates, areas, and conditions for compliance with requirements affecting performance of roofing system.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Clean and remove from substrate sharp projections, dust, debris, moisture, and other substances detrimental to roofing installation in accordance with roofing system manufacturer's written instructions.

Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.

Prime surface of concrete deck with asphalt primer at a rate recommended by roofing manufacturer and allow primer to dry.

Proceed with installation only after unsatisfactory conditions have been corrected.

Re-roof Preparation

Remove all roofing membrane, surfacing, coverboards, insulation, fasteners, asphalt, pitch, adhesives, etc.

Remove an area no larger than can be re-roofed in one day.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.

Install decking to match existing as directed by Owner's Representative.

Raise (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Nail top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Proceed with installation only after unsatisfactory conditions have been corrected.

Recover Preparation

Prepare existing roof according to roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer, and requirements in this Section.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Disable existing roof membrane by cutting a minimum 5 foot x 5 foot grid pattern.

“Skin” existing membrane at substrate.

Remove existing membrane at fasteners.

Remove and replace wet, deteriorated or damaged roof insulation and decking as identified in moisture survey.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.  Install decking to match existing as directed by Owner's Representative.

Raise, (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Nail top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Prime existing cap sheet to prepare for recover application.

Proceed with installation only after unsatisfactory conditions have been corrected.

SUBSTRATE BOARD INSTALLATION

Install substrate board with long joints in continuous straight lines, perpendicular to roof slopes with end joints staggered between rows.  Tightly butt substrate boards together.

Fasten substrate board to top flanges of steel deck according to recommendations in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten substrate board to top flanges of steel deck to resist uplift pressure at corners, perimeter, and field of roof according to roofing system manufacturer's written instructions.

Proceed with installation only after unsatisfactory conditions have been corrected.

VAPOR-RETARDER INSTALLATION

Install 2 glass-fiber felt plies lapping each sheet 19 inches (483 mm) over preceding sheet.  Embed each sheet in a solid mopping of hot roofing asphalt.  Glaze-coat completed surface with hot roofing asphalt.  Apply hot roofing asphalt at a rate of 20 lb/100 sq. ft. (1 kg/sq. m), plus or minus 25 percent.

Retain all subparagraphs below for torched SBS vapor barrier installation.

Install modified bituminous vapor retarder sheet according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, installing as follows:

Torch apply vapor retarder to substrate according to roofing system manufacturer’s instruction.

Adhere vapor retarder in a full mopping of hot asphalt to substrate according to roofing system manufacturer’s instruction.

Self adhere vapor retarder to substrate according to roofing system manufacturer’s instruction.

Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

Repair tears and voids in laps and lapped seams not completely sealed.

Always retain below.  To function effectively, vapor retarders or air barriers must prevent air movement into membrane roofing system.

Install polyethylene-sheet vapor retarder as a loosely laid single layer over area to receive vapor retarder, side and end lapping each sheet a minimum of 2 inches (50 mm) and 6 inches (150 mm), respectively.

Seal side and end laps with [tape] [adhesive].

Completely seal vapor retarder at terminations, obstructions, and penetrations to prevent air movement into membrane roofing system.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSULATION INSTALLATION

Coordinate installation of roof system components so insulation and cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with roofing system manufacturer's written instructions for installation of roof insulation and cover board.

Install tapered insulation under area of roofing to conform to slopes indicated.

Install insulation boards with long joints in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with like material.

Install one or more layers of insulation under area of roofing to achieve required thickness.  Where overall thickness is X.X inches (XX mm) or greater, install 2 or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches (150 mm) in each direction.

Trim surface of insulation boards where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Preliminarily Fastened Insulation for Mechanically Fastened Systems:  Install insulation with fasteners at rate required by roofing system manufacturer or applicable authority, which ever is more stringent.

Adhered Insulation:  Install each layer of insulation and cover board and adhere to substrate as follows:

Install each layer in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Install each layer in a solid mopping of hot roofing asphalt according to roofing system manufacturer’s instruction.

Loose Laid Insulation:  Loose lay all layers of insulation with staggered joints.

Install all layers according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Install all layers to resist uplift pressure at corners, perimeter, and field of roof.

Loose Laid Insulation with Top Insulation Layer Mechanically Fastened:  Loose lay insulation with staggered joints and secure top layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type to deck type.

Fasten top layer according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten top layer to resist uplift pressure at corners, perimeter, and field of roof.

Mechanically Fastened with Subsequent Layers Adhered Insulation:  Secure first layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type to deck type.

Fasten first layer according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten first layer to resist uplift pressure at corners, perimeter, and field of roof.

Install subsequent layers in a cold fluid-applied adhesive according to roofing system manufacturer’s instruction.

Install subsequent layers in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Install subsequent layers in a solid mopping of hot roofing asphalt according to roofing system manufacturer’s instruction.

Proceed with installation only after unsatisfactory conditions have been corrected.

Cover board installation

Coordinate installing membrane roofing system components so cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with membrane roofing system manufacturer's written instructions for installing roof cover board.

Install cover board with long joints of cover board in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with cover board.

Cut and fit cover board within 1/4 inch (6 mm) of nailers, projections, and penetrations.

Trim surface of cover board where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Preliminarily Fastened Insulation for Mechanically Fastened Systems:  Install insulation with fasteners at rate required by roofing system manufacturer or applicable authority, which ever is more stringent.

Adhered Cover Board:  Adhere cover board to substrate as follows:

Install in a solid mopping of hot roofing asphalt according to roofing system manufacturer’s instruction.

Install in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Mechanically Fastened Cover Board:  Install each layer of cover board and secure to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof cover board to deck type.

Fasten according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

Fasten to resist uplift pressure at corners, perimeter, and field of roof.

Proceed with installation only after unsatisfactory conditions have been corrected.

ROOFING MEMBRANE INSTALLATION, GENERAL

Install roofing membrane in accordance with roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer and requirements in this Section.

Start installation of roofing membrane in presence of roofing system manufacturer's technical personnel.

Where roof slope exceeds 1/2 inch per 12 inches (1:24, contact the membrane manufacturer for installation instructions regarding installation direction and backnailing

Cooperate with testing and inspecting agencies engaged or required to perform services for installing roofing system.

Coordinate installing roofing system so insulation and other components of the roofing membrane system not permanently exposed are not subjected to precipitation or left uncovered at the end of the workday or when rain is imminent.

Provide tie-offs at end of each day's work to cover exposed roofing membrane sheets and insulation with a course of coated felt set in roofing cement or hot roofing asphalt with joints and edges sealed.

Complete terminations and base flashings and provide temporary seals to prevent water from entering completed sections of roofing system.

Remove and discard temporary seals before beginning work on adjoining roofing.

Proceed with installation only after unsatisfactory conditions have been corrected.

ADHERED ROOFING MEMBRANE INSTALLATION

Install roofing membrane over area to receive roofing in accordance with membrane roofing system manufacturer's written instructions.  Unroll roofing membrane and allow to relax before installing.

Install sheet in accordance with ASTM D 5036 and roofing system manufacturer’s written instructions.

Start installation of roofing membrane in presence of membrane roofing system manufacturer's technical representative.

Accurately align roofing membrane and maintain uniform side and end laps of minimum dimensions required by manufacturer.  Stagger end laps.

Bonding Adhesive:  Apply solvent-based bonding adhesive to substrate and underside of roofing membrane at rate required by manufacturer and allow to partially dry before installing roofing membrane.  Do not apply bonding adhesive to splice area of roofing membrane.

Bonding Adhesive:  Apply water-based bonding adhesive to substrate at rate required by manufacturer and immediately install roofing membrane.  Do not apply bonding adhesive to splice area of roofing membrane.

Asphalt Application:  Adhere to substrate in a solid mopping of hot asphalt applied at not less than EVT.

Install membrane using either roll or fold method.  Refer to Johns Manville Single Ply Binder for details.

“Broom” the sheet in to ensure full contact.  Do not walk on membrane.

Urethane Membrane Adhesive:  Apply 2-Part Urethane Adhesive substrate at rate required by manufacturer and install fleece-backed roofing membrane.  Do not apply bonding adhesive to splice area of roofing membrane.

Mechanically fasten roofing membrane securely at terminations, penetrations, and perimeter of roofing.

Apply roofing membrane with side laps shingled with slope of roof deck where possible.

Adhesive Seam Installation:  Clean both faces of splice areas, apply splicing cement, and firmly roll side and end laps of overlapping roofing membranes according to manufacturer's written instructions to ensure a watertight seam installation.  Apply lap sealant and seal exposed edges of roofing membrane terminations.

Apply a continuous bead of in-seam sealant before closing splice if required by membrane roofing system manufacturer.

Seams:  Clean seam areas, overlap roofing membrane, and hot-air weld side and end laps of roofing membrane according to manufacturer's written instructions to ensure a watertight seam installation.

Test lap edges with probe to verify seam weld continuity.  Apply lap sealant to seal cut edges of roofing membrane.

Verify field strength of seams a minimum of twice daily and repair seam sample areas.

Remove and repair any unsatisfactory sections before proceeding with Work.

Repair tears, voids, and lapped seams in roofing membrane that do not meet requirements.

Spread sealant or mastic bed over deck drain flange at deck drains and securely seal roofing membrane in place with clamping ring.

Install roofing membrane and auxiliary materials to tie in to existing roofing.

Proceed with installation only after unsatisfactory conditions have been corrected.

BASE FLASHING INSTALLATION

Install sheet flashings and preformed flashing accessories and adhere to substrates in accordance with membrane roofing system manufacturer's written instructions.

Apply solvent-based bonding adhesive to substrate and underside of sheet flashing at required rate and allow to partially dry.  Do not apply bonding adhesive to seam area of flashing.

Flash penetrations and field-formed inside and outside corners with sheet flashing.

Flash penetrations and field-formed inside and outside corners with cured or uncured sheet flashing.

Clean seam areas and overlap and firmly roll sheet flashings into the adhesive.  Weld side and end laps to ensure a watertight seam installation.

Terminate and seal top of sheet flashings and mechanically anchor to substrate through termination bars.

Proceed with installation only after unsatisfactory conditions have been corrected.

WALKWAY INSTALLATION

Flexible Walkways:  Install walkway products in locations indicated.  Adhere with compatible adhesive and heat weld walkway products to substrate according to roofing system manufacturer's written instructions. – PVC

Roof-Paver Walkways:  Install walkway roof pavers according to manufacturer's written instructions in locations indicated, to form walkways.  Leave 3 inches (75 mm) of space between adjacent roof pavers.

Proceed with installation only after unsatisfactory conditions have been corrected.

FIELD QUALITY CONTROL

Testing Agency:  Owner will engage a qualified independent testing and inspecting agency to perform roof tests and inspections and to prepare test reports.

Final Roof Inspection:  Arrange for roofing system manufacturer's Registered Roof Observer (RRO) to inspect roofing installation on completion and submit report to Architect.

Repair or remove and replace components of roofing system where test results or inspections indicate that they do not comply with specified requirements.

PROTECTION AND CLEANING

Protect roofing system from damage and wear during remainder of construction period.

Clean overspray and spillage from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

END OF SECTION 075419