Any time you see the format of [X] [X], for example ([3/4” Fesco Board] [1/2” Retro-Plus Board], choose one of the options and erase the other.  When the specification is complete, change all the bold text to normal.  Then remove all of the brackets ([ and

Every Johns Manville product listed in Part 2 is hyperlinked directly to the specific address on www.jm.com.  Ctrl + Left Mouse Click will take you there.

SECTION 075216 - STYRENE-BUTADIENE-STYRENE (SBS) MODIFIED BITUMINOUS MEMBRANE ROOFING

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

SECTION INCLUDES

SBS-modified bituminous membrane roofing.

Cover board.

Roof insulation.

Vapor retarder.

Base sheet.

Related Sections

Edit as required.

Division 07 Section "Sheet Metal Flashing and Trim" for metal roof penetration flashings, flashings, and counterflashings.

Division 22 Section "Storm Drainage Piping Specialties" for roof drains.

REFERENCES

Roofing Terminology:  Refer to the following publications for definitions of roofing work related terms in this Section:

ASTM D 1079 “Terminology Relating to Roofing and Waterproofing.”

Glossary of NRCA's "The NRCA Roofing and Waterproofing Manual.”

Roof Consultants Institute “Glossary of Roofing Terms”

Sheet Metal Terminology and Techniques:  SMACNA Architectural Sheet Metal Manual.

Retain below for roofing asphalt complying with ASTM D 312.

DESIGN Criteria

General:  Installed roofing membrane system shall remain watertight; and resist specified wind uplift pressures, thermally induced movement, and exposure to weather without failure.

Material Compatibility:  Roofing materials shall be compatible with one another under conditions of service and application required, as demonstrated by roofing system manufacturer based on testing and field experience.

Retain below for projects designed per ASCE 7.

Wind Uplift Performance:  Roofing system shall be identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist wind uplift pressure calculated in accordance with ASCE-7.

Field-of-Roof Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Perimeter Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Corner Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

SUBMITTALS

Product Data:  Manufacturer’s data sheets for each product to be provided.

Detail Drawings:  Provide roofing system plans, elevations, sections, details, and details attachment to other Work, including:

Adjust list below to suit Project.

Base flashings, cants, and membrane terminations.

Tapered insulation, including slopes.

Crickets, saddles, and tapered edge strips, including slopes.

Insulation fastening patterns.

Verification Samples:  Provide for each product specified.

Maintenance Data:  Refer to Johns Manville’s latest published documents on www.JM.com.

Guarantees:  Provide manufacturer’s current guarantee specimen.

QUALITY ASSURANCE

Installer Qualifications:  A qualified firm that is approved, authorized, or licensed by roofing system manufacturer to install manufacturer's product and that is eligible to receive the specified manufacturer's guarantee.

Manufacturer Qualifications:  Qualified manufacturer that has a [UL listing] for roofing system identical to that used for this Project.

Retain paragraph below if testing agency desired and Contractor selects testing agency.

Testing Agency Qualifications:  An independent testing agency with the experience and capability to conduct the testing indicated, as documented according to ASTM E 548.

Test Reports:

Roof drain and leader test or submit plumber’s verification.

Core cut (if requested).

Roof deck fastener pullout test.

Retain moisture survey subparagraphs below for all re-roof and re-cover applications.

Moisture Survey:

Submit prior to installation, results of a non-destructive moisture test of roof system completed by approved third party.  Utilize one of the approved methods:

Infrared Thermography

Nuclear Backscatter

Source Limitations:  Obtain all components from the single source roofing system manufacturer guaranteeing the roofing system.  All products used in the system shall be labeled by the single source roofing manufacturer issuing the guarantee.

Retain subparagraph below for any project requiring torch application of membrane or flashing.

Fire-Test-Response Characteristics:  Roofing materials shall comply with the fire-test-response characteristics indicated as determined by testing identical products per test method below by [UL] or another testing and inspecting agency acceptable to authorities having jurisdiction.  Materials shall be identified with appropriate markings of applicable testing and inspecting agency.

If UL required, edit UL Fire requirements below.

Exterior Fire-Test Exposure:  Class [A] [B] [C]; ASTM E 108, for application and roof slopes indicated.

Fire-Resistance Ratings:  ASTM E 119, for fire-resistance-rated roof assemblies of which roofing system is a part.

DELIVERY, STORAGE, AND HANDLING

Deliver roofing materials in original containers with seals unbroken and labeled with manufacturer's name, product brand name and type, date of manufacture, and directions for storage.

Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.

Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

Handle and store roofing materials and place equipment in a manner to avoid permanent deflection of deck.

PROJECT CONDITIONS

Weather Limitations:  Proceed with installation only when current and forecasted weather conditions permit roofing system to be installed in accordance with manufacturer's written instructions and guarantee requirements.

guarantee

Provide manufacturer's system guarantee equal to Johns Manville's Peak Advantage No Dollar Limit Roofing System Guarantee.

Retain options in subparagraph below based on those used on Project.  Verify availability of manufacturer's total-system warranty and components included.

Single-Source special guarantee includes roofing plies, base flashings, liquid applied flashing, roofing membrane accessories, [granule surfaced roofing membrane] [roof insulation], [fasteners], [cover board], [vapor retarder], [walkway products], [manufacturer’s expansion joints], [manufacturer’s edge metal products], and other single-source components of roofing system marketed by the manufacturer.

Insert correct guarantee term.  Contact Johns Manville Technical to verify.

Guarantee Period:  [10] [15] [20] years from date of Substantial Completion.

Installer’s Guarantee:  Submit roofing Installer's guarantee, signed by Installer, covering Work of this Section, including all components of roofing system, for the following guarantee period:

Guarantee Period:  [Two] [Five] Years from date of Substantial Completion.

PRODUCTS

Base ply and cap-SHEET MATERIALS

Edit as required.

Roofing Membrane Sheet:  [ASTM D 6164, Grade S, Type I, polyester-reinforced] [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] [ASTM D 6162, Grade S, type II, composite polyester- and glass-fiber-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaLastic 180 S] [DynaBase] [DynaBase PR] [DynaPly T1] [DynaGrip Base P/SA] DynaGrip Base SA/SA [DynaGrip Base SD/SA] [DynaMop GL 2.2 P/S] [DynaMop 2.2 PR P/S]

Roofing Membrane Cap Sheet:  [ASTM D 6164, Grade G, Type [I] or [II], polyester-reinforced] [ASTM D 6163, Grade G, Type I, glass-fiber-reinforced] [ASTM D 6162, Grade G, Type II, composite polyester- and glass-fiber-reinforced], SBS-modified asphalt sheet; granular surfaced; suitable for application method specified.  Basis of Design: [DynaLastic 180] [DynaLastic 180 FR] [DynaLastic 180 FR CR] [DynaLastic 180 FR CR G] [DynaLastic 250] [DynaLastic 250 FR] [DynaLastic 250 FR CR] [DynaLastic 250 FR CR G] [DynaGlas] [DynaGlas 30 FR] [DynaGlas FR] [DynaGlas FR CR] [DynaGlas FR CR G] [DynaKap FR T1] [DynaKap FR T1 CR] [DynaKap FR T1 CR G] [DynaKap T1]

BASE SHEET MATERIALS

Glass-Fiber Base Sheet:  [ASTM D4897, Type II, asphalt coated, fiberglass venting base sheet] [ASTM D4601, Type II, asphalt coated, fiberglass base felt].   Basis of Design:  [Ventsulation Felt] [PermaPly 28]

The term "glass-fiber base-ply sheet" is used in this Section to distinguish this part of roofing system from a conventional base sheet and from one- or two-ply, SBS-modified bituminous roofing membranes.  Edit as required.

Glass-Fiber Base Sheet:  ASTM D 2178, Type [IV] [VI], asphalt-impregnated, glass-fiber felt.   Basis of Design:  [GlasPly IV] [GlasPly Premier]

SBS Modified Base Sheet: [ASTM D 6164, Grade S, [Type I] [Type II] polyester-reinforced] [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] [ASTM D 6162, Grade S, Type II, composite polyester- and glass-fiber-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaLastic 180 S] [DYNAFAST 180 HW] [DynaFast 180 S] [DynaFast 250 HW]

FLASHING SHEET MATERIALS

Select backer sheet if required behind exposed flashing sheet.  Contact Johns Manville Technical for flashing detail assistance.

Retain below if coated backer sheet to be mechanically fastened over wood sheathed parapet.

Backer Sheet:  ASTM D 4601, Type II, asphalt-impregnated and -coated, glass-fiber sheet, dusted with fine mineral surfacing on both sides.  Basis of Design: PermaPly 28

Select backer sheet from paragraph below for first ply of a two-ply, SBS-modified bituminous flashing membrane.  Contact Johns Manville Technical for flashing detail assistance.

Backer Sheet:  [ASTM D 6164, Grade S, Type I, polyester-reinforced] [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] [ASTM D 6162, Grade S, Type II, composite polyester- and glass-fiber-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaLastic 180 S] [DynaBase] [DynaBase PR]  [DynaPly T1] [DynaPly T1] [DynaGrip Base P/SA] DynaGrip Base SA/SA [DynaGrip Base SD/SA] [DynaMop GL 2.2 P/S] [DynaMop 2.2 PR P/S] [JM BaseGrip SD/SA]

Choose a granule surfaced flashing sheet below.  Specify “CR” flashing sheet if specifying “CR” membrane.

Flashing Sheet:  [ASTM D 6164, Grade G, Type II, polyester-reinforced] [ASTM D 6163, Grade G, Type I, glass-fiber-reinforced] [ASTM D 6221, Grade G, Type I, composite polyester- and glass-fiber-reinforced] [ASTM D 6298, embossed aluminum foil surfaced, glass-fiber-reinforced], SBS-modified asphalt sheet; granular surfaced; suitable for application method specified.  Basis of Design:  [DynaFlex] [DynaFlex CR] [DynaFlex CR G] [DynaClad] [DynaClad Copper]

Retain below for all applications.  PermaFlash is included in the JM Peak Advantage NDL Guarantee.

Liquid Applied Flashing: A liquid and fabric reinforced flashing system created with a stitch bonded polyester scrim and a two-component, moisture cured, elastomeric, liquid applied flashing material, consisting of an asphalt extended urethane base material and an activator.  Basis of Design:  PermaFlash System

AUXILIARY ROOFING Materials

General:  Auxiliary materials recommended by roofing system manufacturer for intended use and compatible with built-up roofing.

Roofing Asphalt:  ASTM D 312, Type [III] [IV].

Retain paragraph below if asphalt roofing cement is used to adhere flashings or integral metal sheet flashings.

Asphalt Primer:  ASTM D 41.  Basis of Design:  Asphalt Primer

Asphalt Roofing Cement:  ASTM D 4586, type I, asbestos free, of consistency required by roofing system manufacturer for application.  Basis of Design:  Bestile Industrial Roof Cement

Retain paragraph below if adhering base flashing or membrane in cold-applied adhesives.

Cold-Applied Adhesive:  ASTM D3019, Type III, Grade 2. asphalt-based, asbestos-free, cold-applied adhesive specially formulated for compatibility and use with membrane applications.  Basis of Design:  MBR Cold Application Adhesive

Cold-Applied Adhesive:  Roofing system manufacturer's asphalt-based, two-component, asbestos-free, cold-applied adhesive specially formulated for compatibility and use with membrane applications.  Basis of Design:  MBR Bonding Adhesive

Cold-Applied Adhesive:  One-part, elastomeric cold-application adhesive specially formulated for compatibility and use with membrane applications. Basis of Design: Premium Cold Application Adhesive

Cold-Applied Flashing Adhesive:  Roofing system manufacturer's asphalt-based, two-component, asbestos-free, trowel-grade, cold-applied adhesive specially formulated for compatibility and use with flashing applications.  Basis of Design:  MBR Flashing Cement

Cold-Applied Flashing Adhesive:  Roofing system manufacturer's asphalt-based, two-component, asbestos-free, trowel-grade, cold-applied adhesive specially formulated for compatibility and use with flashing applications.  Basis of Design:  MBR Utility Cement

Retain first paragraph below if sealant is needed for moving joints in sheet metal accessories or for certain locations where asphalt roofing cement may be inadequate or undesirable.

Mastic Sealant:  As required by Johns Manville.

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roofing membrane components to substrate, tested by manufacturer for required pullout strength, and provided by the roofing system manufacturer.  Basis of Design: [UltraFast Fasteners and Plates] [All Purpose Fasteners and Plates]

Retain paragraph below if field-applied granules are required for incidental repairs or to coat “bleed-out” in cap sheet systems.

Roofing Granules:  Ceramic-coated roofing granules matching specified cap sheet, provided by roofing system manufacturer. CR Roofing Granules

Coating: Acrylic elastomeric coating with unique bleed-blocking properties particularly well suited for coating over asphalt surfaces.  Basis of Design:  JM CR Seam Coating

Miscellaneous Accessories:  Provide miscellaneous accessories recommended by roofing system manufacturer.

Reflective coating

Elastomeric Coating:  ASTM D 6083.  A multipurpose, acrylic elastomeric coating for use over a variety of substrates with bleed-blocking properties for coating over asphalt surfaces.  Basis of Design: [TopGard 4000] [TopGard 5000]

WALKWAYS

Edit as  required.

Walkway Pads:  Mineral-granule-surfaced, reinforced modified asphalt composition, slip-resisting pads, manufactured as a traffic pad for foot traffic provided by roofing system manufacturer, with a pad size of 32 inch x 32 inch.  Basis of Design: [DynaTred Walkway]

Cover board

Select RetroPlus Board for hot asphalt applications, select DuraBoard products for cold adhesive applications.

Perlite Board: ASTM C 728, Type [1] [2] [3]; composed of expanded perlite, cellulosic fibers, binders and waterproofing agents with top surface seal-coated.  Basis of Design: [RetroPlus Roof Board] [1/2" DuraBoard] [3/4" DuraBoard] [1" DuraBoard]

Gypsum Board:  ASTM C 1278, non-faced, gypsum and cellulose fiber substrate, [1/4 inch (6 mm)] [1/2 inch (13 mm)] [5/8 inch (16 mm)] thick.  Basis of Design: JM Securock Gypsum-Fiber Roof Board

## rOOF INSULATION

### General:  Provide preformed roof insulation boards that comply with requirements and referenced standards, selected from manufacturer's standard sizes and of thicknesses indicated.

### Polyisocyanurate Board Insulation:  ASTM C 1289, Type  II, Class [1] [2] [3], Grade [2 (20 psi)] [3 (25 psi)], Basis of Design: [ENRGY 3] [ENRGY 3 25 PSI] [ENRGY 3 CGF] [ENRGY 3 25 PSI CGF] [ENRGY 3 AGF] [ENRGY 3 25 PSI AGF] [ENRGY 3 FR] [ENRGY 3 25 PSI FR]

Choose performance standard or prescriptive thickness.

#### Provide insulation package with minimum R Value: [insert R Value] [minimum required by applicable code].

#### Provide insulation package with minimum thickness: [insert thickness].

#### Provide insulation package in multiple layers.

#### Minimum Long-Term Thermal Resistance (LTTR): 5.7 per inch.

##### Determined in accordance with CAN/ULC S770 at 75ºF (24ºC)

Edit as required.  Coordinate insulation selection and thicknesses indicated on Drawings with adjoining construction, Johns Manville Guarantee requirements, as well as, HVAC design and energy program.

## Tapered insulation

Retain paragraph below if tapered insulation is required.  Contact Johns Manville Tapered Department for tapered designs and estimates.

### Tapered Insulation:  ASTM C 1289, Type II, Class [1] [2] [3], Grade [2 (20 psi)] [3 (25 psi)], provide factory-tapered insulation boards fabricated to slope of [1/4 inch per 12 inches (1:48)] <Insert slope>, unless otherwise indicated.  Basis of Design: [Tapered ENRGY 3] [Tapered ENRGY 3 25 PSI] [Tapered ENRGY 3 CGF] [Tapered ENRGY 3 25 PSI CGF] [Tapered ENRGY 3 AGF] [Tapered ENRGY 3 25 PSI AGF] [Tapered ENRGY 3 FR] [Tapered ENRGY 3 25 PSI FR]

## INSULATION ACCESSORIES

### General:  Roof insulation accessories recommended by insulation manufacturer for intended use and compatible with membrane roofing.

### Provide factory preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for sloping to drain.  Fabricate to slopes indicated. Basis of Design: [DiamondBack Pre-Cut Crickets] [DiamondBack Pre-Cut Miters] [Tapered Fesco Edge Strip]

### Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roof insulation to substrate, and furnished by roofing system manufacturer. Basis of Design: UltraFast Fasteners and Plates

### Urethane Adhesive:  Manufacturer’s two component polyurethane adhesive formulated to adhere insulation to substrate.  Basis of Design:  [JM Two-Part Urethane Insulation Adhesive (UIA)] [JM Green Two-Part Urethane Insulation Adhesive] [JM One-Step Foamable Adhesive] [Roofing Systems Urethane Adhesive (RSUA)]

### One Part Urethane Adhesive: Manufacturer’s one component polyurethane adhesive formulated to adhere insulation to substrate. Basis of Design:  Urethane Insulation Adhesive

### Insulation Cant Strips:  ASTM C 728, perlite insulation board.  Basis of Design: FesCant Plus

### Wood Nailer Strips:  Comply with requirements in Division 06 Section "Miscellaneous Rough Carpentry".

## VAPOR RETARDER

Delete this Article if vapor retarders are not required.  Review compatibility of vapor retarder with other roofing system materials. Retain substrate board or layer of insulation for steel deck.

### Glass-Fiber Felts:  ASTM D 2178, Type IV, asphalt-impregnated, glass-fiber felt.  Basis of Design:  GlasPly IV

### Torch Applied SBS Vapor Retarder: [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced [ASTM D 6164, Grade S, Type I, polyester-reinforced], SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaWeld Base] [DynaBase HW] [DynaWeld 180 S]

### Self-Adhered SBS Vapor Retarder:  [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced], SBS-modified asphalt sheet; sand surfaced; suitable for application method specified. Basis of Design: DynaGrip SD/SA

### Self-Adhered SBS Vapor Retarder: Tri-laminate woven polyethylene, nonslip UV protected top surface; suitable for application method specified. Basis of Design: JM Vapor Barrier SA

### Polyethylene Vapor Retarder:  ASTM D 4397, [6 mils (0.15 mm)] [10 mils (0.25 mm)] thick, minimum, with maximum permeance rating of 0.13 perm (7.5 ng/Pa x s x sq. m).

#### Tape:  Pressure-sensitive tape of type recommended by vapor-retarder manufacturer for sealing joints and penetrations in vapor retarder.

#### Adhesive:  Manufacturer's standard lap adhesive

      - AUXILIARY ROOFING System Components

Retain all if applicable.

Expansion Joints: Provide factory fabricated weatherproof, exterior covers for expansion joint openings consisting of flexible rubber membrane, supported by a closed cell foam to form flexible bellows, with two metal flanges, adhesively and mechanically combined to the bellows by a bifurcation process.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Expand-O-Flash] [Expand-O-Gard]

Coping System:  Manufacturer’s factory fabricated coping consisting of a base piece and a snap-on cap.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  Presto-Lock Coping

Fascia System:  Manufacturer’s factory fabricated fascia consisting of a base piece and a snap-on cover.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Presto Lock Fascia] [Presto-Tite Fascia]

Metal Edge System: Manufacturer’s factory fabricated metal edge system used to terminate the roof at the perimeter of the structure. Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design: Presto Stop Gravel Stop

Metal Flashing Sheet:  Metal flashing sheet is specified in Division 07 Section "Sheet Metal Flashing and Trim."

EXECUTION

EXAMINATION

General:

#### Blocking, curbs, and nailers are required at edges of roof penetrations, area dividers, and terminations.

Verify that roof openings and penetrations are in place and set and braced and that roof drains are securely clamped in place.

Verify that wood cants, blocking, curbs, and nailers are securely anchored to roof deck at penetrations and terminations and that nailers match thicknesses of insulation.

#### Retain or revise first two subparagraphs and associated subparagraph below for concrete roof decks.

Concrete Decks:

Verify that concrete curing compounds that will impair adhesion of roofing components to roof deck have been removed.

Verify that concrete substrate is visibly dry and free of moisture.

Ensure general rigidity and proper slope for drainage.

Verify that deck is secured with no projecting fasteners and with no adjacent units in excess of 1/16 inch (1.6 mm) out of plane relative to adjoining deck.

Unacceptable panels should be brought to the attention of the General Contractor and Project Owner’s Representative and must be corrected prior to installation of roofing system.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Clean and remove from substrate sharp projections, dust, debris, moisture, and other substances detrimental to roofing system installation in accordance with roofing system manufacturer's written instructions.

Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.

Retain paragraph below if priming concrete deck before installing overlying roofing system.

If applicable, prime surface of deck with asphalt primer at a rate recommended by roofing manufacturer and allow primer to dry.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Re-roof Preparation

Retain Article for Re-Roof applications.  Remove for new construction or recovers.

Remove all roofing membrane, surfacing, coverboards, insulation, fasteners, asphalt, pitch, adhesives, etc.

Remove an area no larger than can be re-roofed in one day.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.

If applicable, repair decking to match existing as directed by Owner's Representative.

Raise (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Secure top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Recover Preparation

Prepare existing roof according to roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer, and requirements in this Section.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Choose one option below for disabling existing roof.

        - Disable existing roof membrane by cutting a minimum 10 foot x 10 foot grid pattern.

Remove existing membrane per manufacturer’s written instructions.

Remove and replace wet, deteriorated or damaged roof insulation and decking as identified in moisture survey.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.  Install decking to match existing as directed by Owner's Representative.

Raise, (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Secure top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Prime existing cap sheet to prepare for recover application.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Base-sheet installation

Retain paragraph below if mechanically fastening base sheet to substrate before adhering first layer of insulation.

Install one lapped base sheet course and mechanically fasten to substrate according to roofing system manufacturer's written instructions.

Enhance fastening rate in perimeter and corner zones according to code or manufacturer, whichever is more stringent.

Comply with roofing system manufacturer's written instructions for installing roof insulation.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

VAPOR-RETARDER INSTALLATION

Delete this Article if not required.   Retain one of the subparagraphs below for 2 ply glass-fiber felt vapor barrier installation.

Install polyethylene-sheet vapor retarder as a loosely laid single layer over area to receive vapor retarder, side and end lapping each sheet a minimum of 2 inches (50 mm) and 6 inches (150 mm), respectively.

Seal side and end laps with [tape] [adhesive].

Install 2 glass-fiber felt plies lapping each sheet 19 inches (483 mm) over preceding sheet.  Embed each sheet in a solid mopping of hot roofing asphalt per manufacturer’s written instructions.

Install modified bituminous vapor retarder sheet according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, installing as follows:

Torch-apply vapor retarder to substrate according to roofing system manufacturer’s instruction.

Adhere vapor retarder in a full mopping of hot asphalt to substrate according to roofing system manufacturer’s instruction.

Self-adhere vapor retarder to substrate according to roofing system manufacturer’s instruction.

Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

Retain all.

Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

Repair tears and voids in laps and lapped seams not completely sealed.

Completely seal vapor retarder at terminations, obstructions, and penetrations to prevent air movement into membrane roofing system.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSULATION INSTALLATION

Coordinate installation of roof system components so insulation and cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with roofing system manufacturer's written instructions for installation of roof insulation.

Insulation Cant Strips:  Install and secure preformed 45-degree insulation cant strips at junctures of roofing membrane system with vertical surfaces or angle changes greater than 45 degrees per manufacturer’s instruction.

Retain first subparagraph below if tapered insulation is required.

Install tapered insulation under area of roofing to conform to slopes indicated.

Install insulation boards with long joints in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with like material.

Install 2 or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches (150 mm) in each direction.

Trim surface of insulation boards where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Retain paragraph below if adhering each layer of insulation and cover board.

Adhered Insulation:  Install each layer of insulation and adhere to substrate as follows:

Retain applicable subparagraph below.

Install each layer in a two-part cold fluid-applied adhesive according to roofing system manufacturer’s instruction.

Install each layer in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Retain paragraph below if mechanically fastening layers.

Loose Laid Insulation:  Loose lay all layers of insulation with staggered joints.

Install all layers to resist uplift pressure at corners, perimeter, and field of roof.

Loose Laid Insulation with Top Insulation Layer Mechanically Fastened:  Loose lay insulation with staggered joints and secure top layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type to deck type.

Fasten top layer to resist uplift pressure at corners, perimeter, and field of roof.

Install subsequent layers in a two-part urethane adhesive. Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Cover board installation

Retain Article if cover board is required for project.

Coordinate installing membrane roofing system components so cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with membrane roofing system manufacturer's written instructions for installing roof cover board.

Install cover board with long joints of cover board in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with cover board.

Cut and fit cover board within 1/4 inch (6 mm) of nailers, projections, and penetrations.

Trim surface of cover board where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Retain paragraph below if adhering cover board.  Applicable with “Adhered Insulation” and “Mechanically Fastened with Subsequent Layers Adhered” Insulation.

Adhered Cover Board:  Adhere cover board to substrate as follows:

Install using a cold fluid-applied adhesive according to roofing system manufacturer’s instruction.

Install in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

ROOFING MEMBRANE INSTALLATION, GENERAL

Install roofing membrane in accordance with roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer and requirements in this Section.

Delete paragraph below if not a Johns Manville Guaranteed project.

Start installation of roofing membrane in presence of roofing system manufacturer's technical personnel.

Retain paragraph and subparagraph below if roof slope exceeds minimum permitted by roofing system manufacturer.

Where roof slope exceeds 1/2 inch per 12 inches (1:24, contact the membrane manufacturer for installation instructions regarding installation direction and backnailing

Cooperate with testing and inspecting agencies engaged or required to perform services for installing roofing system.

Coordinate installing roofing system so insulation and other components of the roofing membrane system not permanently exposed are not subjected to precipitation or left uncovered at the end of the workday or when rain is imminent.

Provide tie-offs at end of each day's work to cover exposed roofing membrane sheets and insulation with a course of coated felt set in roofing cement or hot roofing asphalt with joints and edges sealed.

Complete terminations and base flashings and provide temporary seals to prevent water from entering completed sections of roofing system.

Remove and discard temporary seals before beginning work on adjoining roofing.

Retain subparagraph below for hot asphalt applications only.

Substrate-Joint Penetrations:  Prevent roofing asphalt from penetrating substrate joints, entering building, or damaging roofing system components or adjacent building construction.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

SBS-MODIFIED BITUMINOUS MEMBRANE INSTALLATION

Install [one] [two] modified bituminous roofing membrane sheet[s] [and] [cap sheet] according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, with one of the following installing methods:

          - Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

Select one of three subparagraphs below for installation technique.

Adhere to substrate in cold-applied adhesive according to roofing system manufacturer’s instruction.

Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

Repair tears and voids in laps and lapped seams not completely sealed.

Apply roofing granules to cover exuded bead at laps while bead is hot.

Install roofing membrane sheets so side and end laps shed water.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

FLASHING AND STRIPPING INSTALLATION

Install base flashing over cant strips and other sloping and vertical surfaces, at roof edges, and at penetrations through roof, and secure to substrates according to roofing system manufacturer's written instructions and as follows:

Smooth surfaces of masonry, concrete walls, parapets and the like require priming before applying hot asphalt or cold adhesive.

Prime substrates with asphalt primer if required by roofing system manufacturer.

Retain one of three subparagraphs below if a single backer sheet is required behind flashing sheet.  Retain first for backer sheets mechanically fastened to wood-surfaced walls or parapets and second or third for adhered backer sheets.  Keep consistent with membrane application.

Backer Sheet Application:  Mechanically fasten backer sheet to walls or parapets.

Backer Sheet Application:  Install backer sheet and adhere to substrate in approved adhesive applied at rate required by roofing system manufacturer.

Flashing Sheet Application:  Adhere flashing sheet to substrate in approved adhesive applied at rate required by roofing system manufacturer.

Flashing Sheet Application:  Adhere flashing sheet to substrate in approved asphalt roofing cement; apply cement at rate required by roofing system manufacturer.

Extend base flashing up walls or parapets a minimum of 8 inches (200 mm) above roofing membrane and 4 inches (100 mm) onto field of roofing membrane.

Mechanically fasten top of base flashing securely at terminations and perimeter of roofing.

Delete subparagraph below if temporarily sealing upper termination of flashings awaiting counterflashing.  Retain option if specifying termination seal.

Seal top termination of base flashing with a strip of glass-fiber fabric set in MBR Flashing cement.

Delete below if no interior roof drains.  Choose either lead sheet or PermaFlash.

Roof Drains:  Set [30-by-30-inch (760-by-760-mm)] <Insert size> 4 lb lead flashing sheet in a bed of MBR Flashing Cement on completed roofing membrane.  Cover metal flashing with roofing membrane cap-sheet stripping and extend a minimum of 4 inches (100 mm) beyond edge of metal flashing onto field of roofing membrane.  Clamp roofing membrane, metal flashing, and stripping into roof-drain clamping ring.

Roof Drains:  Flash drain using PermaFlash system.  Clamp roofing membrane, flashing, and stripping into roof-drain clamping ring.

Install stripping according to roofing system manufacturer's written instructions.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

Coating Installation

Ensure that all surfaces are clean, dry and free of any dirt, grease, oil or other debris that may interfere with proper adhesion.

Apply coating to roofing membrane and base flashings as recommended by the manufacturer using [approved spray apparatus] [1/4” notched squeegee].  Apply in two coats allowing the first coat to completely dry before applying the second coat.

WALKWAY INSTALLATION

Retain this Article if walkways set directly on roofing membrane are required.

Walkway Pads:  Install walkway pads using units of size indicated or, if not indicated, of manufacturer's standard size according to walkway pad manufacturer's written instructions.

Retain subparagraph below for aggregate-surfaced roofing membrane; delete if smooth-surfaced roofing membrane is required.

Sweep away loose aggregate surfacing and set walkway pads in additional flood coat of hot roofing asphalt.

Walkway Cap Sheet Strips:  Install roofing membrane walkway cap sheet strips over roofing membrane [in hot roofing asphalt] [in cold-applied adhesive] [by torch application].

Roof-Paver Walkways:  Install walkway roof pavers according to manufacturer's written instructions in locations indicated, to form walkways.  Leave 3 inches (75 mm) of space between adjacent roof pavers.

Retain for all.

Proceed with installation only after unsatisfactory conditions have been corrected.

FIELD QUALITY CONTROL

Retain if required.

Testing Agency:  Owner will engage a qualified independent testing and inspecting agency to perform roof tests and inspections and to prepare test reports.

A roof inspection is required by Johns Manville before issuance of Johns Manville Peak Advantage Guarantee.

Final Roof Inspection:  Arrange for roofing system manufacturer's Registered Roof Observer (RRO) to inspect roofing installation on completion and submit report to Architect.

Repair or remove and replace components of roofing system where test results or inspections indicate that they do not comply with specified requirements.

Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

PROTECTION AND CLEANING

Protect roofing system from damage and wear during remainder of construction period.

Clean overspray and spillage from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

END OF SECTION 075216