SECTION 075216 - STYRENE-BUTADIENE-STYRENE (SBS) MODIFIED BITUMINOUS MEMBRANE ROOFING

GENERAL

SECTION INCLUDES

SBS-modified bituminous membrane roofing.

Cover board.

Roof insulation.

Vapor retarder.

Related Sections

Division 06 Section "Miscellaneous Rough Carpentry" for wood nailers, cants, curbs, and blocking.

Division 07 Section "Sheet Metal Flashing and Trim" for metal roof penetration flashings, flashings, and counterflashings.

Division 07 Section "Manufactured Roof Expansion Joints."

Division 22 Section "Storm Drainage Piping Specialties" for roof drains.

REFERENCES

Roofing Terminology:  Refer to the following publications for definitions of roofing work related terms in this Section:

ASTM D 1079 “Terminology Relating to Roofing and Waterproofing.”

Glossary of NRCA's "The NRCA Roofing and Waterproofing Manual.”

Roof Consultants Institute “Glossary of Roofing Terms” for definition of terms related to roofing work in this Section.

Sheet Metal Terminology and Techniques:  SMACNA Architectural Sheet Metal Manual.

DESIGN Criteria

General:  Installed roofing membrane system shall remain watertight; and resist specified wind uplift pressures, thermally induced movement, and exposure to weather without failure.

Material Compatibility:  Roofing materials shall be compatible with one another under conditions of service and application required, as demonstrated by roofing system manufacturer based on testing and field experience.

Wind Uplift Performance:  Roofing system shall be identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist wind uplift pressure calculated in accordance with ASCE-7.

Field-of-Roof Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Perimeter Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

Corner Uplift Pressure:  <Insert number> lbf/sq. ft. (kN/sq. m).

FMG Listing:  Roofing membrane, base flashings, and component materials shall comply with requirements in FMG 4450 and FMG 4470 as part of a roofing system and that are listed in FMG's “RoofNav" for Class 1 or noncombustible construction, as applicable.  Identify materials with FMG markings.

Roofing system shall comply with RoofNav #:

Fire/Windstorm Classification:  Class 1A-Insert number (starting at 60 and incrementing by 15)

Hail Resistance:  [MH] [SH].

LEED Credits:

Roofing system shall be eligible for LEED Credit SS 7.1 and/or SS 7.2.

Insulation and cover board materials shall contribute to LEED credit MR 4.1.

Insulation package shall contribute to LEED EA credit.

Materials with minimal VOC shall contribute to LEED credit EQ 4.

EPA Energy Star:

Roofing membrane shall achieve an initial reflectance of greater than 0.65 and a three year aged reflectance of greater than 0.50.

T24/CRRC-1:

Roofing system shall comply with the requirements of Title 24.

Roofing membrane shall be tested by CRRC-1.

SUBMITTALS

Product Data:  Manufacturer’s data sheets for each product to be provided.

Detail Drawings:  Provide roofing system plans, elevations, sections, details, and details attachment to other Work, including:

Base flashings, cants, and membrane terminations.

Tapered insulation, including slopes.

Crickets, saddles, and tapered edge strips, including slopes.

Insulation fastening patterns.

Verification Samples:  Provide for each product specified.

Maintenance Data:  Refer to Johns Manville’s latest published documents on www.specJM.com.

Guarantees:  Special guarantees specified in this Section.

QUALITY ASSURANCE

Installer Qualifications:  A qualified firm that is approved, authorized, or licensed by roofing system manufacturer to install manufacturer's product and that is eligible to receive the specified manufacturer's guarantee.

Manufacturer Qualifications:  A qualified manufacturer that has [UL listing] [FMG approval] for roofing system identical to that used for this Project.

Testing Agency Qualifications:  An independent testing agency with the experience and capability to conduct the testing indicated, as documented according to ASTM E 548.

Test Reports:

Roof drain and leader test or submit plumber’s verification.

Core cut (if requested).

Roof deck fastener pullout test.

Moisture Survey:

Submit prior to installation, results of a non-destructive moisture test of roof system completed by approved third party.  Utilize one of the approved methods:

Infrared Thermography

Nuclear Backscatter

Source Limitations:  Obtain all components from the single source roofing system manufacturer guaranteeing the roofing system.  All products used in the system shall be labeled by the single source roofing manufacturer issuing the guarantee.

Fire-Test-Response Characteristics:  Provide roofing materials with the fire-test-response characteristics indicated as determined by testing identical products per test method below by UL[, FMG,] or another testing and inspecting agency acceptable to authorities having jurisdiction.  Materials shall be identified with appropriate markings of applicable testing and inspecting agency.

Exterior Fire-Test Exposure:  Class  [A] [B] [C]; ASTM E 108, for application and roof slopes indicated.

Fire-Resistance Ratings:  ASTM E 119, for fire-resistance-rated roof assemblies of which roofing system is a part.

DELIVERY, STORAGE, AND HANDLING

Deliver roofing materials in original containers with seals unbroken and labeled with manufacturer's name, product brand name and type, date of manufacture, and directions for storage.

Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.

Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

Handle and store roofing materials and place equipment in a manner to avoid permanent deflection of deck.

PROJECT CONDITIONS

Weather Limitations:  Proceed with installation only when current and forecasted weather conditions permit roofing system to be installed in accordance with manufacturer's written instructions and guarantee requirements.

guarantee

Provide manufacturer's system guarantee equal to Johns Manville's Peak Advantage No Dollar Limit Roofing System Guarantee.

Single-Source special guarantee includes roofing plies, base flashings, liquid applied flashing, roofing membrane accessories, [granule surfaced roofing membrane] [roof insulation], [fasteners], [cover board], [vapor retarder], [walkway products], [manufacturer’s expansion joints], [manufacturer’s edge metal products], and other single-source components of roofing system marketed by the manufacturer.

Guarantee Period:  [10] [15] [20] years from date of Substantial Completion.

Wind Rider:  Guarantee shall not exclude coverage for wind events up to [number between 55 - 120] mph.

Hail Rider:   Guarantee shall have no exclusions for hail events up to [1 inch] [1.5 inches] [2 inches]

Accidental Puncture Rider: Guarantee shall provide coverage for accidental puncture for up to [8] [16] billed repair hours per year for the life of the guarantee.

Installer’s Guarantee:  Submit roofing Installer's guarantee, signed by Installer, covering Work of this Section, including all components of roofing system, for the following guarantee period:

Guarantee Period:  [Two] [Five] Years from date of Substantial Completion.

PRODUCTS

SBS-MODIFIED ASPHALT-SHEET MATERIALS

Roofing Membrane Sheet:  [ASTM D 6164, Grade S, Type I, polyester-reinforced] SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaLastic 180 S] [or architect pre approved equal]

Roofing Membrane Cap Sheet:  [ASTM D 6164, Grade G, Type [I] or [II], polyester-reinforced] SBS-modified asphalt sheet; granular surfaced; suitable for application method specified.  Basis of Design: [DynaLastic 180 FR] [DynaLastic 180 FR CR] [DynaLastic 250 FR] [DynaLastic 250 FR CR [or architect pre approved equal]

BASE FLASHING SHEET MATERIALS - SBS

Backer Sheet:  ASTM D 4601, Type  II, asphalt-impregnated and -coated, glass-fiber sheet, dusted with fine mineral surfacing on both sides.  Basis of Design: PermaPly 28 [or architect pre approved equal]

Backer Sheet:  [ASTM D 6164, Grade S, Type I, polyester-reinforced] SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design: [DynaLastic 180 S]  [or architect pre approved equal]

Flashing Sheet:  [ASTM D 6164, Grade G, Type  II, polyester-reinforced [ASTM D 6298, embossed aluminum foil surfaced, glass-fiber-reinforced], SBS-modified asphalt sheet; granular surfaced; suitable for application method specified.  Basis of Design:  [DynaLastic 250 FR] [DynaLastic 250 FR CR [DynaFlex] [DynaFlex CR] [DynaClad] [or architect pre approved equal]

Liquid Applied Flashing: A liquid and fabric reinforced flashing system created with a stitchbonded polyester scrim and a two-component, moisture cured, elastomeric, liquid applied flashing material, consisting of an asphalt extended urethane base material and an activator.  Basis of Design:  PermaFlash System [or architect pre approved equal]

AUXILIARY ROOFING MEMBRANE - Bituminous

General:  Auxiliary materials recommended by roofing system manufacturer for intended use and compatible with built-up roofing.

Asphalt Primer:  ASTM D 41.  Basis of Design:  Asphalt Primer [or architect pre approved equal]

Asphalt Roofing Cement:  ASTM D 4586, asbestos free, of consistency required by roofing system manufacturer for application.  Basis of Design:  Bestile Industrial Roof Cement or architect pre approved equal]

Cold-Applied Adhesive:  Roofing system manufacturer's asphalt-based, two-component, asbestos-free, cold-applied adhesive specially formulated for compatibility and use with membrane applications.  Basis of Design:  MBR Bonding Adhesive [or architect pre approved equal]

Cold-Applied Flashing Adhesive:  Roofing system manufacturer's asphalt-based, two-component, asbestos-free, trowel-grade, cold-applied adhesive specially formulated for compatibility and use with flashing applications.  Basis of Design:  MBR Flashing Cement [or architect pre approved equal]

Mastic Sealant:  As required by Johns Manville.

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roofing membrane components to substrate, tested by manufacturer for required pullout strength, and provided by the roofing system manufacturer.  Basis of Design: [UltraFast Fasteners and Plates] [All Purpose Fasteners and Plates] [or architect pre approved equal]

Roofing Granules:  Ceramic-coated roofing granules matching specified cap sheet, provided by roofing system manufacturer.

Coating: Acrylic elastomeric coating with unique bleed-blocking properties particularly well suited for coating over asphalt surfaces.  Basis of Design:  JM CR Seam Coating [or architect pre approved equal]

Miscellaneous Accessories:  Provide miscellaneous accessories recommended by roofing system manufacturer.

AUXILIARY ROOFING System Components

Expansion Joints: Provide factory fabricated weatherproof, exterior covers for expansion joint openings consisting of flexible rubber membrane, supported by a closed cell foam to form flexible bellows, with two metal flanges, adhesively and mechanically combined to the bellows by a bifurcation process.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Expand-O-Flash] [Expand-O-Gard] [or architect pre approved equal]

Coping System:  Manufacturer’s factory fabricated coping consisting of a base piece and a snap-on cap.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  Presto-Lock Coping [or architect pre approved equal]

Fascia System:  Manufacturer’s factory fabricated fascia consisting of a base piece and a snap-on cover.  Provide product manufactured and marketed by single-source membrane supplier that is included in the No Dollar Limit guarantee.  Basis of Design:  [Presto Lock Fascia] [Presto-Tite Fascia] [or architect pre approved equal]

Metal Flashing Sheet:  Metal flashing sheet is specified in Division 07 Section "Sheet Metal Flashing and Trim."

Reflective and waterproof coating

Elastomeric Coating:  ASTM D 6083.  A multipurpose, acrylic elastomeric coating for use over a variety of substrates with bleed-blocking properties for coating over asphalt surfaces.  Basis of Design: [TopGard 4000] [TopGard 5000] [or architect pre approved equal]

WALKWAYS

Walkway Pads:  Mineral-granule-surfaced, reinforced modified asphalt composition, slip-resisting pads, manufactured as a traffic pad for foot traffic provided by roofing system manufacturer, with a pad size of 32 inch x 32 inch.  Basis of Design: [Johns Manville DynaTred] [Johns Manville DynaTred Plus] [or architect pre approved equal]

Cover board

Perlite Board: ASTM C 728; composed of expanded perlite, cellulosic fibers, binders and waterproofing agents with top surface seal-coated.  Basis of Design: : [1/2" DuraBoard] [3/4" DuraBoard] [1" DuraBoard] [or architect pre approved equal]

ROOF INSULATION

General:  Preformed roof insulation boards that comply with requirements and referenced standards, selected from manufacturer's standard sizes and of thicknesses indicated.

Polyisocyanurate Board Insulation:  ASTM C 1289, Type  II, Basis of Design: ENRGY 3 [or architect pre approved equal]

Provide insulation package with R Value greater than [19] [insert R Value] [minimum required by applicable code].

Provide insulation package with minimum thickness [insert thickness].

Tapered insulation

Tapered Insulation:  ASTM C 1289, provide factory-tapered insulation boards fabricated to slope of [1/4 inch per 12 inches (1:48)] <Insert slope>, unless otherwise indicated.  Basis of Design: Tapered ENRGY 3 [or architect pre approved equal]

INSULATION ACCESSORIES

General:  Roof insulation accessories recommended by insulation manufacturer for intended use and compatible with membrane roofing.

Provide factory preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for sloping to drain.  Fabricate to slopes indicated. Basis of Design: [Tapered Pre-Cut Cricket] [Tapered Pre-Cut Miter] [Tapered Fesco Edge Strip] [or architect pre approved equal]

Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roof insulation to substrate, and furnished by roofing system manufacturer. Basis of Design: [UltraFast Fasteners and Plates] [UltraFast Pre-Assembled Fasteners] [UltraFast AccuTrac Fastener and Plate System] [or architect pre approved equal]

Cold Fluid-Applied Adhesive:  Manufacturer's No VOC, two-component cold fluid-applied adhesive formulated to adhere roof insulation to substrate.  Basis of Design:  MBR Bonding Adhesive [or architect pre approved equal]

Urethane Adhesive:  Manufacturer’s two component urethane adhesive formulated to adhere insulation to substrate.  Basis of Design:  [JM Two-Part Urethane Insulation Adhesive] [JM Green Two-Part Urethane Insulation Adhesive] [or architect pre approved equal]

Insulation Cant Strips:  ASTM C 728, perlite insulation board.  Basis of Design: FesCant Plus [or architect pre approved equal]

Wood Nailer Strips:  Comply with requirements in Division 06 Section "Miscellaneous Rough Carpentry."

VAPOR RETARDER

SBS Vapor Retarder :  [ASTM D 6163, Grade S, Type I, glass-fiber-reinforced] SBS-modified asphalt sheet; smooth surfaced; suitable for application method specified. Basis of Design[DynaBase] [or architect pre approved equal]

EXECUTION

EXAMINATION

Examine substrates, areas, and conditions for compliance with requirements affecting performance of roofing system:

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Clean and remove from substrate sharp projections, dust, debris, moisture, and other substances detrimental to roofing installation in accordance with roofing system manufacturer's written instructions.

Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.

Prime surface of concrete deck with asphalt primer at a rate recommended by roofing manufacturer and allow primer to dry.

Proceed with installation only after unsatisfactory conditions have been corrected.

Re-roof Preparation

Remove all roofing membrane, surfacing, coverboards, insulation, fasteners, asphalt, pitch, adhesives, etc.

Remove an area no larger than can be re-roofed in one day.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.

Install decking to match existing as directed by Owner's Representative.

Raise (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Nail top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Proceed with installation only after unsatisfactory conditions have been corrected.

Recover Preparation

Prepare existing roof according to roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer, and requirements in this Section.

Tear out all base flashings, counterflashings, pitch pans, pipe flashings, vents and like components necessary for application of new membrane.

Disable existing roof membrane by cutting a minimum 5 foot x 5 foot grid pattern.

“Skin” existing membrane at substrate.

Remove existing membrane at fasteners.

Remove and replace wet, deteriorated or damaged roof insulation and decking as identified in moisture survey.

Remove abandoned equipment curbs, skylights, smoke hatches, and penetrations.  Install decking to match existing as directed by Owner's Representative.

Raise, (disconnect by licensed craftsmen, if necessary) all HVAC units and other equipment supported by curbs to conform with the following:

Modify curbs as required to provide a minimum 8" base flashing height measured from the surface of the new membrane to the top of the flashing membrane.

Nail top of flashing and install new metal counterflashing prior to re-installation of unit.

Perimeter nailers must be elevated to match elevation of new roof insulation.

Immediately remove all debris from roof surface.  Demolished roof system may not be stored on the roof surface.

Prime existing cap sheet to prepare for recover application.

Proceed with installation only after unsatisfactory conditions have been corrected.

VAPOR-RETARDER INSTALLATION

Install modified bituminous vapor retarder sheet according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, installing as follows:

Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

Repair tears and voids in laps and lapped seams not completely sealed.

Completely seal vapor retarder at terminations, obstructions, and penetrations to prevent air movement into membrane roofing system.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSULATION INSTALLATION

Coordinate installation of roof system components so insulation and cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with roofing system manufacturer's written instructions for installation of roof insulation and cover board.

Insulation Cant Strips:  Install and secure preformed 45-degree insulation cant strips at junctures of roofing membrane system with vertical surfaces or angle changes greater than 45 degrees per manufacturer’s instruction.

Install tapered insulation under area of roofing to conform to slopes indicated.

Install insulation boards with long joints in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with like material.

Install one or more layers of insulation under area of roofing to achieve required thickness.  Where overall thickness is X.X inches (XX mm) or greater, install 2 or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches (150 mm) in each direction.

Trim surface of insulation boards where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Adhered Insulation:  Install each layer of insulation and cover board and adhere to substrate as follows:

Install each layer in a two-part cold fluid-applied adhesive according to roofing system manufacturer’s instruction.

Install each layer in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Proceed with installation only after unsatisfactory conditions have been corrected.

Cover board installation

Coordinate installing membrane roofing system components so cover board is not exposed to precipitation or left exposed at the end of the workday.

Comply with membrane roofing system manufacturer's written instructions for installing roof cover board.

Install cover board with long joints of cover board in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with cover board.

Cut and fit cover board within 1/4 inch (6 mm) of nailers, projections, and penetrations.

Trim surface of cover board where necessary at roof drains so completed surface is flush and does not restrict flow of water.

Install tapered edge strips at perimeter edges of roof that do not terminate at vertical surfaces.

Preliminarily Fastened Insulation for Mechanically Fastened Systems:  Install insulation with fasteners at rate required by roofing system manufacturer or applicable authority, which ever is more stringent.

Adhered Cover Board:  Adhere cover board to substrate as follows:

Install using a cold fluid-applied adhesive according to roofing system manufacturer’s instruction.

Install in a two-part urethane adhesive according to roofing system manufacturer’s instruction.

Proceed with installation only after unsatisfactory conditions have been corrected.

ROOFING MEMBRANE INSTALLATION, GENERAL

Install roofing membrane in accordance with roofing system manufacturer's written instructions, applicable recommendations of the roofing manufacturer and requirements in this Section.

Start installation of roofing membrane in presence of roofing system manufacturer's technical personnel.

Where roof slope exceeds 1/2 inch per 12 inches (1:24, contact the membrane manufacturer for installation instructions regarding installation direction and backnailing

Cooperate with testing and inspecting agencies engaged or required to perform services for installing roofing system.

Coordinate installing roofing system so insulation and other components of the roofing membrane system not permanently exposed are not subjected to precipitation or left uncovered at the end of the workday or when rain is imminent.

Provide tie-offs at end of each day's work to cover exposed roofing membrane sheets and insulation with a course of coated felt set in roofing cement or hot roofing asphalt with joints and edges sealed.

Complete terminations and base flashings and provide temporary seals to prevent water from entering completed sections of roofing system.

Remove and discard temporary seals before beginning work on adjoining roofing.

Substrate-Joint Penetrations:  Prevent roofing asphalt from penetrating substrate joints, entering building, or damaging roofing system components or adjacent building construction.

Proceed with installation only after unsatisfactory conditions have been corrected.

SBS-MODIFIED BITUMINOUS MEMBRANE INSTALLATION

Install two modified bituminous roofing membrane sheets and cap sheet according to roofing manufacturer's written instructions, starting at low point of roofing system.  Extend roofing membrane sheets over and terminate beyond cants, installing as follows:

Adhere to substrate in cold-applied adhesive according to roofing system manufacturer’s instruction.

Unroll roofing membrane sheets and allow them to relax for minimum time period required by manufacturer.

Laps:  Accurately align roofing membrane sheets, without stretching, and maintain uniform side and end laps.  Stagger end laps.  Completely bond and seal laps, leaving no voids.

Repair tears and voids in laps and lapped seams not completely sealed.

Apply roofing granules to cover exuded bead at laps while bead is hot.

Install roofing membrane sheets so side and end laps shed water.

Proceed with installation only after unsatisfactory conditions have been corrected.

FLASHING AND STRIPPING INSTALLATION

Install base flashing over cant strips and other sloping and vertical surfaces, at roof edges, and at penetrations through roof, and secure to substrates according to roofing system manufacturer's written instructions and as follows:

Prime substrates with asphalt primer if required by roofing system manufacturer.

Backer Sheet Application:  Install backer sheet and adhere to substrate in approved adhesive applied at rate required by roofing system manufacturer.

Backer Sheet Application:  Install backer sheet and self adhere to substrate as required by roofing system manufacturer.

Flashing Sheet Application:  Adhere flashing sheet to substrate in approved adhesive applied at rate required by roofing system manufacturer.

Flashing Sheet Application:  Adhere flashing sheet to substrate in approved asphalt roofing cement; apply cement at rate required by roofing system manufacturer.

Extend base flashing up walls or parapets a minimum of 8 inches (200 mm) above roofing membrane and 4 inches (100 mm) onto field of roofing membrane.

Mechanically fasten top of base flashing securely at terminations and perimeter of roofing.

Seal top termination of base flashing with a strip of glass-fiber fabric set in MBR Flashing cement.

Roof Drains:  Set [30-by-30-inch (760-by-760-mm)] <Insert size> 4 lb lead flashing sheet in a bed of MBR Flashing Cement on completed roofing membrane.  Cover metal flashing with roofing membrane cap-sheet stripping and extend a minimum of 4 inches (100 mm) beyond edge of metal flashing onto field of roofing membrane.  Clamp roofing membrane, metal flashing, and stripping into roof-drain clamping ring.

Roof Drains:  Flash drain using PermaFlash system.  Clamp roofing membrane, flashing, and stripping into roof-drain clamping ring.

Install stripping according to roofing system manufacturer's written instructions.

Proceed with installation only after unsatisfactory conditions have been corrected.

Coating Installation

Ensure that all surfaces are clean, dry and free of any dirt, grease, oil or other debris that may interfere with proper adhesion.

Apply coating to roofing membrane and base flashings as recommended by the manufacturer using [approved spray apparatus] [1/4” notched squeegee].  Apply in two coats allowing the first coat to completely dry before applying the second coat.

WALKWAY INSTALLATION

Walkway Pads:  Install walkway pads using units of size indicated or, if not indicated, of manufacturer's standard size according to walkway pad manufacturer's written instructions.

Sweep away loose aggregate surfacing and set walkway pads in additional flood coat of hot roofing asphalt.

Walkway Cap Sheet Strips:  Install roofing membrane walkway cap sheet strips over roofing membrane [in hot roofing asphalt] [in cold-applied adhesive] [by torch application]. – SBS

Roof-Paver Walkways:  Install walkway roof pavers according to manufacturer's written instructions in locations indicated, to form walkways.  Leave 3 inches (75 mm) of space between adjacent roof pavers.

Proceed with installation only after unsatisfactory conditions have been corrected.

FIELD QUALITY CONTROL

Testing Agency:  Owner will engage a qualified independent testing and inspecting agency to perform roof tests and inspections and to prepare test reports.

Final Roof Inspection:  Arrange for roofing system manufacturer's Registered Roof Observer (RRO) to inspect roofing installation on completion and submit report to Architect.

Repair or remove and replace components of roofing system where test results or inspections indicate that they do not comply with specified requirements.

Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

PROTECTION AND CLEANING

Protect roofing system from damage and wear during remainder of construction period.

Clean overspray and spillage from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

END OF SECTION 075216